## SUMMARY
AC LOAD SUMMARY OF PSP HOSPITAL(SERVICE BLOCK) - RITHVIK CONSULTANTS, CHENNAI
S.NO | FLOOR | DESCRIPTION OF ROOM | ROOM DIMENSION |  |  | ROOM AREA | EQUIPMENT LOAD(KW) | NO OF PEOPLE | NO.OF FRESH AIR CHANGES | DEHUMIDIFIED CFM | ACTUAL TONNAGE | RECOMMENDED TONNAGE | LIGHT LOAD
|  |  | L | B | H | SQ FT
GROUND FLOOR
1 | GROUND FLOOR | CSSD | 20.336 | 9.84 | 11.48 | 200.1062 | 0.5 | 5 | 0 | 552.4581 | 1.2604 | 1.5 | 200.1062
2 |  | CSSD MANAGER | 20.336 | 9.84 | 11.48 | 200.1062 | 1 | 4 | 0 | 640.2112 | 1.3349 | 1.5 | 200.1062
|  | TOTAL |  |  |  | 400.2125 | 1.5 | 9 | 0 | 1192.6693 | 2.5953 | 3
FIRST FLOOR
3 | FIRST FLOOR | WAITING | 19.68 | 23.616 | 11.48 | 464.7629 | 0.5 | 6 | 0 | 655.7117 | 1.6246 | 1.5 | 464.7629
4 |  | LOBBY | 30.504 | 19.68 | 11.48 | 600.3187 | 0.5 | 6 | 0 | 747.1271 | 1.9765 | 2 | 600.3187
5 |  | MEDICAL STORE | 67.568 | 38.704 | 11.48 | 2615.1519 | 10 | 5 | 0 | 3854.5294 | 7.6584 | 8 | 2615.1519
6 |  | AIRLOCK | 10.824 | 9.512 | 11.48 | 102.9579 | 0.5 | 2 | 0 | 411.8622 | 0.85572 | 1 | 102.9579
7 |  | CENTRAL RESEARCH LAB | 45.592 | 38.704 | 11.48 | 1764.5928 | 10 | 20 | 0 | 3636.1167 | 8.2189 | 8.5 | 1764.5928
8 |  | CENTRAL RESEARCH LAB FACULTY | 19.68 | 11.48 | 11.48 | 225.9264 | 1 | 6 | 0 | 615.6857 | 1.5692 | 1.5 | 225.9264
9 |  | CENTRAL RESEARCH LAB E.LIBRARY | 20.992 | 19.68 | 11.48 | 413.1226 | 1 | 8 | 0 | 687.1442 | 1.7653 | 2 | 413.1226
10 |  | CENTRAL RESEARCH LAB PREP.STORE | 19.024 | 11.48 | 11.48 | 218.3955 | 1 | 4 | 0 | 703.0346 | 1.4414 | 1.5 | 218.3955
|  | TOTAL |  |  |  | 6405.2286 | 24.5 | 57 | 0 | 11311.2117 | 25.11 | 26 | 6405.2286
SECOND FLOOR
11 | SECOND FLOOR | PRIVATE ROOM 1 | 34.768 | 19.68 | 11.48 | 684.2342 | 1 | 3 | 2 | 1204.2987 | 3.7353 | 4 | 684.2342
12 |  | PRIVATE ROOM 2 | 34.768 | 19.024 | 11.48 | 661.4264 | 1 | 3 | 2 | 748.2552 | 2.9733 | 3 | 661.4264
13 |  | PRIVATE ROOM 3 | 34.768 | 19.188 | 11.48 | 667.1284 | 1 | 3 | 2 | 1042.5876 | 3.4408 | 3.5 | 667.1284
14 |  | PRIVATE ROOM 4 | 34.768 | 19.352 | 11.48 | 672.8303 | 1 | 3 | 2 | 917.1387 | 3.2634 | 3 | 672.8303
15 |  | PRIVATE ROOM 5 | 34.768 | 19.352 | 11.48 | 672.8303 | 1 | 3 | 2 | 993.8291 | 3.3813 | 3.5 | 672.8303
16 |  | PRIVATE ROOM 6 | 34.768 | 19.352 | 11.48 | 672.8303 | 1 | 3 | 2 | 1272.436 | 3.8093 | 4 | 672.8303
17 |  | PRIVATE ROOM 7 | 30.176 | 19.352 | 11.48 | 583.966 | 1 | 3 | 2 | 1077.4262 | 3.2706 | 3 | 583.966
17 |  | PRIVATE ROOM 8 | 30.176 | 19.352 | 11.48 | 583.966 | 1 | 3 | 2 | 917.1732 | 3.0244 | 3 | 583.966
18 |  | PRIVATE ROOM 9 | 30.176 | 19.352 | 11.48 | 583.966 | 1 | 3 | 2 | 956.5213 | 3.0848 | 3 | 583.966
19 |  | PRIVATE ROOM 10 | 30.176 | 18.368 | 11.48 | 554.2728 | 1 | 3 | 2 | 891.5084 | 2.9051 | 3 | 554.2728
20 |  | PRIVATE ROOM 11 | 30.176 | 19.352 | 11.48 | 583.966 | 1 | 3 | 2 | 917.1732 | 3.0244 | 3 | 583.966
21 |  | PRIVATE ROOM 12 | 30.176 | 19.352 | 11.48 | 583.966 | 1 | 3 | 2 | 917.1732 | 3.0244 | 3 | 583.966
22 |  | PRIVATE ROOM 13 | 30.176 | 19.352 | 11.48 | 583.966 | 1 | 3 | 2 | 917.1732 | 3.0244 | 3 | 583.966
23 |  | PRIVATE ROOM 14 | 30.176 | 19.352 | 11.48 | 583.966 | 1 | 3 | 2 | 1286.3651 | 3.5916 | 3.5 | 583.966
|  | TOTAL |  |  |  | 8673.3145 | 14 | 42 | 28 | 14059.0592 | 45.5531 | 45.5
THIRD FLOOR
18 | THIRD FLOOR | COLD STORAGE | 11.48 | 9.84 | 11.48 | 112.9632 | 2 | 3 | 0 | 891.5362 | 1.6814 | 2 | 112.9632
19 |  | PREPARATION ROOM | 19.024 | 18.04 | 11.48 | 343.193 | 0.5 | 4 | 0 | 1058.0612 | 2.1468 | 2 | 343.193
20 |  | DISINFECTION AIRLOCK | 19.024 | 9.84 | 11.48 | 187.1962 | 0.2 | 2 | 0 | 747.6101 | 1.4178 | 1.5 | 187.1962
21 |  | PRE PCR | 22.304 | 19.352 | 11.48 | 431.627 | 2 | 5 | 0 | 1348.443 | 2.6104 | 2.5 | 431.627
22 |  | PCR ASSAY ROOM | 21.648 | 19.352 | 11.48 | 418.9321 | 2 | 5 | 0 | 1194.8822 | 2.3675 | 2.5 | 418.9321
23 |  | POST PCR | 22.96 | 20.008 | 11.48 | 459.3837 | 2 | 5 | 0 | 1641.5785 | 3.076 | 3.5 | 459.3837
24 |  | SKILL DEVELOPMENT LAB | 73.144 | 21.648 | 11.48 | 1583.4213 | 2 | 20 | 0 | 1539.8994 | 4.8988 | 5 | 1583.4213
25 |  | ROOM 1 | 11.48 | 16.072 | 11.48 | 184.5066 | 0.5 | 3 | 0 | 565.6423 | 1.1514 | 1 | 184.5066
26 |  | ROOM 2 | 11.48 | 9.512 | 11.48 | 109.1978 | 0.5 | 3 | 0 | 321.0908 | 0.73434 | 1 | 109.1978
27 |  | ROOM 3 | 11.48 | 9.512 | 11.48 | 109.1978 | 0.5 | 3 | 0 | 323.6813 | 0.80687 | 0.5 | 109.1978
28 |  | ROOM 4 | 23.288 | 9.512 | 11.48 | 221.5155 | 0.5 | 3 | 0 | 569.9634 | 1.1783 | 1 | 221.5155
29 |  | ROOM 5 | 23.288 | 9.512 | 11.48 | 221.5155 | 0.5 | 3 | 0 | 569.9634 | 1.1783 | 1 | 221.5155
30 |  | ROOM 6 | 23.288 | 9.512 | 11.48 | 221.5155 | 0.5 | 3 | 0 | 569.9634 | 1.1783 | 1 | 221.5155
31 |  | ROOM 7 | 23.288 | 9.512 | 11.48 | 221.5155 | 0.5 | 3 | 0 | 569.9634 | 1.1783 | 1 | 221.5155
32 |  | ROOM 8 | 23.288 | 9.512 | 11.48 | 221.5155 | 0.5 | 3 | 0 | 569.9634 | 1.1783 | 1 | 221.5155
33 |  | ROOM 9 | 23.288 | 9.512 | 11.48 | 221.5155 | 0.5 | 3 | 0 | 756.5775 | 1.4651 | 1.5 | 221.5155
34 |  | ROOM 10 | 59.04 | 23.288 | 11.48 | 1374.9235 | 1 | 10 | 0 | 3236.146 | 6.33 | 6.5 | 1374.9235
35 |  | DEMONSTRATION OF SKILL | 45.264 | 19.68 | 11.48 | 890.7955 | 2 | 5 | 0 | 2813.6002 | 5.2277 | 5.5 | 890.7955
|  | TOTAL |  |  |  | 7534.4303 | 18.2 | 86 | 0 | 19288.566 | 39.8056 | 40
|  | GRAND TOTAL |  |  |  | 23013.1859 | 58.2 | 194 | 28 | 45851.5062 | 113.064 | 114.5
S.NO | FLOOR | DESCRIPTION OF ROOM | ROOM DIMENSION |  |  | ROOM AREA | EQUIPMENT LOAD(KW) | NO OF PEOPLE | NO.OF FRESH AIR CHANGES | DEHUMIDIFIED CFM | ACTUAL TONNAGE | RECOMMENDED TONNAGE | LIGHT LOAD

## CSSD
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 6.2 | 20.336
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 3 | 9.84
Space used for |  | CSSD |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 20.336 | 9.84 | 200.1062 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 20.336
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.84
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 200.1062 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 2297.2196 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 48.1083 | Glass - E | 0 |  | CFM for people | 25
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 5 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 12.0064
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 37.0064
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 11.1019
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 48.1083
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 459.3837 |  | N | 112.9632 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 233.4573 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 112.9632 | 0
Partition wall |  | 459.3837 | Sq ft | 28.6 | 0.4 | 5255.3493 | [5 empty] | Out side air | 48.1083 |  | TOTAL | 459.3837 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 5
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 200.1062
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.2604
Out side air | 0.12 | 48.1083 | Cfm | 33.6 | 1.08 | 209.4904 | [5 empty] | Dehumidifed CFM | 552.4581
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1.5
People |  | 5 | Nos | 240 |  | 1200
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 200.1062 | Watts | 3.413 |  | 682.9626
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 9054.3023 | Room sensible heat - Summer |  |  |  | 10186.0901
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1131.7878 | Room total heat |  |  |  | 11395.1369
Room sensible heat total | [5 empty] | 10186.0901 | Effective sen. heat factor |  |  |  | 0.8939
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 48.1083 | Cfm | 76.2 | 0.68 | 299.1335 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 5 | Nos | 160 |  | 800 | Dehumidifed CFM |  |  |  | 552.4581
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1099.1335
Safety factor |  |  |  |  | 10% | 109.9133
Room latent heat total | [5 empty] | 1209.0468 | AS PER SPECIFICATION - TR |  |  |  | 1.5
Room total heat | [5 empty] | 11395.1369 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 552.4581
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.2604
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 552.4581
OUT SIDE AIR HEAT
Sensible | 0.88 | 48.1083 | Cfm | 33.6 | 1.08 | 1536.2631
Latent | 0.88 | 48.1083 | Cfm | 76.2 | 0.68 | 2193.6455
Grand total heat ( Btu/hr) | [5 empty] | 15125.0455
Tonnage | [5 empty] | 1.2604
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## CSSD MANAGER
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 6.2 | 20.336
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 3 | 9.84
Space used for |  | CSSD MANAGER |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 20.336 | 9.84 | 200.1062 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 20.336
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.84
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 200.1062 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 2297.2196 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 41.6083 | Glass - E | 0 |  | CFM for people | 20
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 4 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 12.0064
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 32.0064
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 9.6019
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 41.6083
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 459.3837 |  | N | 112.9632 | 0
[12 empty] | Partition glass | 0 |  | E | 233.4573 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 112.9632 | 0
Partition wall |  | 459.3837 | Sq ft | 28.6 | 0.4 | 5255.3493 | [5 empty] | Out side air | 41.6083 |  | TOTAL | 459.3837 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 4
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 200.1062
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.3349
Out side air | 0.12 | 41.6083 | Cfm | 33.6 | 1.08 | 181.1858 | [5 empty] | Dehumidifed CFM | 640.2112
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1.5
People |  | 4 | Nos | 240 |  | 960
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 200.1062 | Watts | 3.413 |  | 682.9626
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 10492.4977 | Room sensible heat - Summer |  |  |  | 11804.0599
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1311.5622 | Room total heat |  |  |  | 12792.6486
Room sensible heat total | [5 empty] | 11804.0599 | Effective sen. heat factor |  |  |  | 0.92272
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 41.6083 | Cfm | 76.2 | 0.68 | 258.717 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 4 | Nos | 160 |  | 640 | Dehumidifed CFM |  |  |  | 640.2112
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 898.717
Safety factor |  |  |  |  | 10% | 89.8717
Room latent heat total | [5 empty] | 988.5887 | AS PER SPECIFICATION - TR |  |  |  | 1.5
Room total heat | [5 empty] | 12792.6486 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 640.2112
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.3349
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 640.2112
OUT SIDE AIR HEAT
Sensible | 0.88 | 41.6083 | Cfm | 33.6 | 1.08 | 1328.6957
Latent | 0.88 | 41.6083 | Cfm | 76.2 | 0.68 | 1897.258
Grand total heat ( Btu/hr) | [5 empty] | 16018.6023
Tonnage | [5 empty] | 1.3349
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## WAITING
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 6 | 19.68
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 7.2 | 23.616
Space used for |  | WAITING |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 19.68 | 23.616 | 464.7629 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 19.68
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 23.616
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 464.7629 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 5335.4779 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 75.2515 | Glass - E | 0 |  | CFM for people | 30
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 6 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 27.8858
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 57.8858
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 17.3657
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 75.2515
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 497.0381 |  | N | 271.1117 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 225.9264 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 497.0381 | Sq ft | 28.6 | 0.4 | 5686.1156 | [5 empty] | Out side air | 75.2515 |  | TOTAL | 497.0381 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 6
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 464.7629
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.6246
Out side air | 0.12 | 75.2515 | Cfm | 33.6 | 1.08 | 327.6872 | [5 empty] | Dehumidifed CFM | 655.7117
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1.5
People |  | 6 | Nos | 240 |  | 1440
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 464.7629 | Watts | 3.413 |  | 1586.2357
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 10746.5385 | Room sensible heat - Summer |  |  |  | 12089.8559
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1343.3173 | Room total heat |  |  |  | 13660.5545
Room sensible heat total | [5 empty] | 12089.8559 | Effective sen. heat factor |  |  |  | 0.88502
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 75.2515 | Cfm | 76.2 | 0.68 | 467.9078 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 6 | Nos | 160 |  | 960 | Dehumidifed CFM |  |  |  | 655.7117
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1427.9078
Safety factor |  |  |  |  | 10% | 142.7908
Room latent heat total | [5 empty] | 1570.6986 | AS PER SPECIFICATION - TR |  |  |  | 1.5
Room total heat | [5 empty] | 13660.5545 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 655.7117
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.6246
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 655.7117
OUT SIDE AIR HEAT
Sensible | 0.88 | 75.2515 | Cfm | 33.6 | 1.08 | 2403.0394
Latent | 0.88 | 75.2515 | Cfm | 76.2 | 0.68 | 3431.3241
Grand total heat ( Btu/hr) | [5 empty] | 19494.918
Tonnage | [5 empty] | 1.6246
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## LOBBY
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 9.3 | 30.504
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 6 | 19.68
Space used for |  | LOBBY |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 30.504 | 19.68 | 600.3187 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 30.504
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.68
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 600.3187 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 6891.6589 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 105.3249 | Glass - E | 0 |  | CFM for people | 45
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 6 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 36.0191
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 81.0191
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 24.3057
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 105.3249
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 576.1123 |  | N | 350.1859 | 0
[12 empty] | Partition glass | 0 |  | E | 225.9264 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 576.1123 | Sq ft | 28.6 | 0.4 | 6590.7249 | [5 empty] | Out side air | 105.3249 |  | TOTAL | 576.1123 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 6
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 600.3187
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.9765
Out side air | 0.12 | 105.3249 | Cfm | 33.6 | 1.08 | 458.6434 | [5 empty] | Dehumidifed CFM | 747.1271
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 2
People |  | 6 | Nos | 240 |  | 1440
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 600.3187 | Watts | 3.413 |  | 2048.8878
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 12244.7562 | Room sensible heat - Summer |  |  |  | 13775.3507
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1530.5945 | Room total heat |  |  |  | 15551.7424
Room sensible heat total | [5 empty] | 13775.3507 | Effective sen. heat factor |  |  |  | 0.88578
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 105.3249 | Cfm | 76.2 | 0.68 | 654.9016 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 6 | Nos | 160 |  | 960 | Dehumidifed CFM |  |  |  | 747.1271
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1614.9016
Safety factor |  |  |  |  | 10% | 161.4902
Room latent heat total | [5 empty] | 1776.3917 | AS PER SPECIFICATION - TR |  |  |  | 2
Room total heat | [5 empty] | 15551.7424 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 747.1271
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.9765
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 747.1271
OUT SIDE AIR HEAT
Sensible | 0.88 | 105.3249 | Cfm | 33.6 | 1.08 | 3363.3851
Latent | 0.88 | 105.3249 | Cfm | 76.2 | 0.68 | 4802.6114
Grand total heat ( Btu/hr) | [5 empty] | 23717.7389
Tonnage | [5 empty] | 1.9765
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## MEDICAL STORE
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 20.6 | 67.568
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 11.8 | 38.704
Space used for |  | MEDICAL STORE |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 67.568 | 38.704 | 2615.1519 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 67.568
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 38.704
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 2615.1519 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 30021.9435 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 80 | Sq ft | 12 | 0.56 | 537.6 | Ventilation air quantity cfm |  |  |  | 236.4818 | Glass - E | 80 |  | CFM for people | 25
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 5 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 156.9091
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 181.9091
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 364.3219 |  | SAFETY 30% | 54.5727
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 236.4818
Wall - E |  | 364.3219 | Sq ft | 36.6 | 0.34 | 4533.622 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 80 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 854.7549 |  | N | 150.6176 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 444.3219 | 0
All glass |  | 80 | Sq ft | 33.6 | 1.13 | 3037.44 | [5 empty] | Floor | 0 |  | S | 259.8154 | 0
Partition wall |  | 854.7549 | Sq ft | 28.6 | 0.4 | 9778.3958 | [5 empty] | Out side air | 236.4818 |  | TOTAL | 854.7549 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 5
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 10
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 2615.1519
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 7.6584
Out side air | 0.12 | 236.4818 | Cfm | 33.6 | 1.08 | 1029.7744 | [5 empty] | Dehumidifed CFM | 3854.5294
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 8
People |  | 5 | Nos | 240 |  | 1200
Equipment |  | 10 | KW | 3413 | 1 | 34130
Lights |  | 2615.1519 | Watts | 3.413 |  | 8925.5133
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 63172.3455 | Room sensible heat - Summer |  |  |  | 71068.8887
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 7896.5432 | Room total heat |  |  |  | 73566.3564
Room sensible heat total | [5 empty] | 71068.8887 | Effective sen. heat factor |  |  |  | 0.96605
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 236.4818 | Cfm | 76.2 | 0.68 | 1470.4252 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 5 | Nos | 160 |  | 800 | Dehumidifed CFM |  |  |  | 3854.5294
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 2270.4252
Safety factor |  |  |  |  | 10% | 227.0425
Room latent heat total | [5 empty] | 2497.4677 | AS PER SPECIFICATION - TR |  |  |  | 8
Room total heat | [5 empty] | 73566.3564 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 3854.5294
[7 empty] | AS PER DRAWING - TR |  |  |  | 7.6584
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 3854.5294
OUT SIDE AIR HEAT
Sensible | 0.88 | 236.4818 | Cfm | 33.6 | 1.08 | 7551.6788
Latent | 0.88 | 236.4818 | Cfm | 76.2 | 0.68 | 10783.1181
Grand total heat ( Btu/hr) | [5 empty] | 91901.1534
Tonnage | [5 empty] | 7.6584
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## AIRLOCK
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 3.3 | 10.824
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 2.9 | 9.512
Space used for |  | AIRLOCK |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 10.824 | 9.512 | 102.9579 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 10.824
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.512
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 102.9579 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 1181.9566 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 27.5307 | Glass - E | 0 |  | CFM for people | 15
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 2 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 6.1775
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 21.1775
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 6.3532
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 27.5307
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 357.7168 |  | N | 124.2595 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 109.1978 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 124.2595 | 0
Partition wall |  | 357.7168 | Sq ft | 28.6 | 0.4 | 4092.2802 | [5 empty] | Out side air | 27.5307 |  | TOTAL | 357.7168 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 2
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 102.9579
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 0.85572
Out side air | 0.12 | 27.5307 | Cfm | 33.6 | 1.08 | 119.8842 | [5 empty] | Dehumidifed CFM | 411.8622
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1
People |  | 2 | Nos | 240 |  | 480
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 102.9579 | Watts | 3.413 |  | 351.3953
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 6750.0596 | Room sensible heat - Summer |  |  |  | 7593.8171
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 843.7575 | Room total heat |  |  |  | 8134.1192
Room sensible heat total | [5 empty] | 7593.8171 | Effective sen. heat factor |  |  |  | 0.93358
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 27.5307 | Cfm | 76.2 | 0.68 | 171.1838 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 2 | Nos | 160 |  | 320 | Dehumidifed CFM |  |  |  | 411.8622
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 491.1838
Safety factor |  |  |  |  | 10% | 49.1184
Room latent heat total | [5 empty] | 540.3022 | AS PER SPECIFICATION - TR |  |  |  | 1
Room total heat | [5 empty] | 8134.1192 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 411.8622
[7 empty] | AS PER DRAWING - TR |  |  |  | 0.85572
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 411.8622
OUT SIDE AIR HEAT
Sensible | 0.88 | 27.5307 | Cfm | 33.6 | 1.08 | 879.1504
Latent | 0.88 | 27.5307 | Cfm | 76.2 | 0.68 | 1255.3478
Grand total heat ( Btu/hr) | [5 empty] | 10268.6174
Tonnage | [5 empty] | 0.85572
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## CENTRAL RESEARCH LAB
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 13.9 | 45.592
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 11.8 | 38.704
Space used for |  | CENTRAL RESEARCH LAB |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 45.592 | 38.704 | 1764.5928 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 45.592
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 38.704
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 1764.5928 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 20257.525 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 80 | Sq ft | 12 | 0.56 | 537.6 | Ventilation air quantity cfm |  |  |  | 332.6382 | Glass - E | 80 |  | CFM for people | 150
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 20 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 105.8756
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 255.8756
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 364.3219 |  | SAFETY 30% | 76.7627
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 332.6382
Wall - E |  | 364.3219 | Sq ft | 36.6 | 0.34 | 4533.622 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 80 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 444.3219 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 444.3219 | 0
All glass |  | 80 | Sq ft | 33.6 | 1.13 | 3037.44 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 444.3219 | Sq ft | 28.6 | 0.4 | 5083.0428 | [5 empty] | Out side air | 332.6382 |  | TOTAL | 444.3219 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 20
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 10
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 1764.5928
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 8.2189
Out side air | 0.12 | 332.6382 | Cfm | 33.6 | 1.08 | 1448.4932 | [5 empty] | Dehumidifed CFM | 3636.1167
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 8.5
People |  | 20 | Nos | 240 |  | 4800
Equipment |  | 10 | KW | 3413 | 1 | 34130
Lights |  | 1764.5928 | Watts | 3.413 |  | 6022.5551
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 59592.753 | Room sensible heat - Summer |  |  |  | 67041.8471
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 7449.0941 | Room total heat |  |  |  | 72836.9969
Room sensible heat total | [5 empty] | 67041.8471 | Effective sen. heat factor |  |  |  | 0.92044
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 332.6382 | Cfm | 76.2 | 0.68 | 2068.3179 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 20 | Nos | 160 |  | 3200 | Dehumidifed CFM |  |  |  | 3636.1167
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 5268.3179
Safety factor |  |  |  |  | 10% | 526.8318
Room latent heat total | [5 empty] | 5795.1497 | AS PER SPECIFICATION - TR |  |  |  | 8.5
Room total heat | [5 empty] | 72836.9969 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 3636.1167
[7 empty] | AS PER DRAWING - TR |  |  |  | 8.2189
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 3636.1167
OUT SIDE AIR HEAT
Sensible | 0.88 | 332.6382 | Cfm | 33.6 | 1.08 | 10622.2831
Latent | 0.88 | 332.6382 | Cfm | 76.2 | 0.68 | 15167.6649
Grand total heat ( Btu/hr) | [5 empty] | 98626.9449
Tonnage | [5 empty] | 8.2189
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## CENTRAL RESEARCH LAB FACULTY
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 6 | 19.68
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 3.5 | 11.48
Space used for |  | CENTRAL RESEARCH LAB FACULTY |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 19.68 | 11.48 | 225.9264 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 19.68
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 11.48
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 225.9264 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 2593.6351 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 76.1223 | Glass - E | 0 |  | CFM for people | 45
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 6 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 13.5556
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 58.5556
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 17.5667
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 76.1223
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 131.7904
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 131.7904 | Sq ft | 34.6 | 0.34 | 1550.3823 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 225.9264 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 225.9264 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 225.9264 | Sq ft | 28.6 | 0.4 | 2584.598 | [5 empty] | Out side air | 76.1223 |  | TOTAL | 225.9264 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 6
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 225.9264
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.5692
Out side air | 0.12 | 76.1223 | Cfm | 33.6 | 1.08 | 331.4789 | [5 empty] | Dehumidifed CFM | 615.6857
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1.5
People |  | 6 | Nos | 240 |  | 1440
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 225.9264 | Watts | 3.413 |  | 771.0868
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 10090.546 | Room sensible heat - Summer |  |  |  | 11351.8643
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1261.3183 | Room total heat |  |  |  | 12928.5186
Room sensible heat total | [5 empty] | 11351.8643 | Effective sen. heat factor |  |  |  | 0.87805
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 76.1223 | Cfm | 76.2 | 0.68 | 473.3221 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 6 | Nos | 160 |  | 960 | Dehumidifed CFM |  |  |  | 615.6857
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1433.3221
Safety factor |  |  |  |  | 10% | 143.3322
Room latent heat total | [5 empty] | 1576.6543 | AS PER SPECIFICATION - TR |  |  |  | 1.5
Room total heat | [5 empty] | 12928.5186 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 615.6857
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.5692
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 615.6857
OUT SIDE AIR HEAT
Sensible | 0.88 | 76.1223 | Cfm | 33.6 | 1.08 | 2430.8456
Latent | 0.88 | 76.1223 | Cfm | 76.2 | 0.68 | 3471.0289
Grand total heat ( Btu/hr) | [5 empty] | 18830.3931
Tonnage | [5 empty] | 1.5692
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## CENTRAL RESEARCH LAB E.LIBRARY
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 6.4 | 20.992
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 6 | 19.68
Space used for |  | CENTRAL RESEARCH LAB E.LIBRARY |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 20.992 | 19.68 | 413.1226 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 20.992
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.68
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 413.1226 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 4742.647 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 84.2236 | Glass - E | 0 |  | CFM for people | 40
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 8 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 40 | Sq ft | 12 | 0.56 | 268.8 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 40 |  | CFM for Area basis | 24.7874
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 64.7874
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 19.4362
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 84.2236
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 200.9882
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 200.9882 | Sq ft | 34.6 | 0.34 | 2364.4247 | [5 empty] | All glass | 40 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 0 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 40 | Sq ft | 33.6 | 1.13 | 1518.72 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 0 | Sq ft | 28.6 | 0.4 | 0 | [5 empty] | Out side air | 84.2236 |  | TOTAL | 0 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 8
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 413.1226
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.7653
Out side air | 0.12 | 84.2236 | Cfm | 33.6 | 1.08 | 366.7565 | [5 empty] | Dehumidifed CFM | 687.1442
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 2
People |  | 8 | Nos | 240 |  | 1920
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 413.1226 | Watts | 3.413 |  | 1409.9873
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 11261.6886 | Room sensible heat - Summer |  |  |  | 12669.3996
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1407.7111 | Room total heat |  |  |  | 14653.4645
Room sensible heat total | [5 empty] | 12669.3996 | Effective sen. heat factor |  |  |  | 0.8646
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 84.2236 | Cfm | 76.2 | 0.68 | 523.6954 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 8 | Nos | 160 |  | 1280 | Dehumidifed CFM |  |  |  | 687.1442
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1803.6954
Safety factor |  |  |  |  | 10% | 180.3695
Room latent heat total | [5 empty] | 1984.0649 | AS PER SPECIFICATION - TR |  |  |  | 2
Room total heat | [5 empty] | 14653.4645 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 687.1442
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.7653
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 687.1442
OUT SIDE AIR HEAT
Sensible | 0.88 | 84.2236 | Cfm | 33.6 | 1.08 | 2689.548
Latent | 0.88 | 84.2236 | Cfm | 76.2 | 0.68 | 3840.4326
Grand total heat ( Btu/hr) | [5 empty] | 21183.4451
Tonnage | [5 empty] | 1.7653
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## CENTRAL RESEARCH LAB PREP.STORE
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 5.8 | 19.024
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 3.5 | 11.48
Space used for |  | CENTRAL RESEARCH LAB PREP.STORE |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 19.024 | 11.48 | 218.3955 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 19.024
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 11.48
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 218.3955 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 2507.1806 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 40 | Sq ft | 12 | 0.56 | 268.8 | Ventilation air quantity cfm |  |  |  | 43.0349 | Glass - E | 40 |  | CFM for people | 20
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 4 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 20 | Sq ft | 12 | 0.56 | 134.4 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 20 |  | CFM for Area basis | 13.1037
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 33.1037
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 178.3955 |  | SAFETY 30% | 9.9311
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 43.0349
Wall - E |  | 178.3955 | Sq ft | 36.6 | 0.34 | 2219.9539 | [5 empty] | Wall - S | 111.7904
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 111.7904 | Sq ft | 34.6 | 0.34 | 1315.1023 | [5 empty] | All glass | 60 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 0 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 60 | Sq ft | 33.6 | 1.13 | 2278.08 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 0 | Sq ft | 28.6 | 0.4 | 0 | [5 empty] | Out side air | 43.0349 |  | TOTAL | 0 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 4
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 218.3955
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.4414
Out side air | 0.12 | 43.0349 | Cfm | 33.6 | 1.08 | 187.3978 | [5 empty] | Dehumidifed CFM | 703.0346
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1.5
People |  | 4 | Nos | 240 |  | 960
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 218.3955 | Watts | 3.413 |  | 745.3839
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 11522.1179 | Room sensible heat - Summer |  |  |  | 12962.3826
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1440.2647 | Room total heat |  |  |  | 13960.7286
Room sensible heat total | [5 empty] | 12962.3826 | Effective sen. heat factor |  |  |  | 0.92849
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 43.0349 | Cfm | 76.2 | 0.68 | 267.5873 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 4 | Nos | 160 |  | 640 | Dehumidifed CFM |  |  |  | 703.0346
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 907.5873
Safety factor |  |  |  |  | 10% | 90.7587
Room latent heat total | [5 empty] | 998.346 | AS PER SPECIFICATION - TR |  |  |  | 1.5
Room total heat | [5 empty] | 13960.7286 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 703.0346
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.4414
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 703.0346
OUT SIDE AIR HEAT
Sensible | 0.88 | 43.0349 | Cfm | 33.6 | 1.08 | 1374.2508
Latent | 0.88 | 43.0349 | Cfm | 76.2 | 0.68 | 1962.3066
Grand total heat ( Btu/hr) | [5 empty] | 17297.286
Tonnage | [5 empty] | 1.4414
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 1
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 10.6 | 34.768
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 6 | 19.68
Space used for |  | PRIVATE ROOM 1 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 34.768 | 19.68 | 684.2342 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 34.768
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.68
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 684.2342 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 7855.0091 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 82.6203 | Glass - E | 0 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 261.8336 | Glass - S | 0 |  | CFM for Area basis | 41.0541
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 63.5541
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 19.0662
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 225.9264 |  | MIN FA REQT | 82.6203
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 225.9264 | Sq ft | 30.6 | 0.34 | 2350.5383 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 854.7549 |  | N | 399.1366 | 0
[12 empty] | Partition glass | 0 |  | E | 225.9264 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 97.9014 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 131.7904 | 0
Partition wall |  | 854.7549 | Sq ft | 28.6 | 0.4 | 9778.3958 | [5 empty] | Out side air | 261.8336 |  | TOTAL | 854.7549 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 684.2342
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.7353
Out side air | 0.12 | 261.8336 | Cfm | 33.6 | 1.08 | 1140.1703 | [5 empty] | Dehumidifed CFM | 1204.2987
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 4
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 684.2342 | Watts | 3.413 |  | 2335.2915
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 19737.3958 | Room sensible heat - Summer |  |  |  | 22204.5703
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 2467.1745 | Room total heat |  |  |  | 24523.437
Room sensible heat total | [5 empty] | 22204.5703 | Effective sen. heat factor |  |  |  | 0.90544
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 261.8336 | Cfm | 76.2 | 0.68 | 1628.0606 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 1204.2987
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 2108.0606
Safety factor |  |  |  |  | 10% | 210.8061
Room latent heat total | [5 empty] | 2318.8667 | AS PER SPECIFICATION - TR |  |  |  | 4
Room total heat | [5 empty] | 24523.437 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 1204.2987
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.7353
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 1204.2987
OUT SIDE AIR HEAT
Sensible | 0.88 | 261.8336 | Cfm | 33.6 | 1.08 | 8361.2487
Latent | 0.88 | 261.8336 | Cfm | 76.2 | 0.68 | 11939.1111
Grand total heat ( Btu/hr) | [5 empty] | 44823.7967
Tonnage | [5 empty] | 3.7353
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 2
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 10.6 | 34.768
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.8 | 19.024
Space used for |  | PRIVATE ROOM 2 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 34.768 | 19.024 | 661.4264 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 34.768
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.024
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 661.4264 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 7593.1754 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 80.8413 | Glass - E | 0 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 253.1058 | Glass - S | 0 |  | CFM for Area basis | 39.6856
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 62.1856
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 18.6557
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 218.3955 |  | MIN FA REQT | 80.8413
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 218.3955 | Sq ft | 30.6 | 0.34 | 2272.187 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 218.3955 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 218.3955 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 218.3955 | Sq ft | 28.6 | 0.4 | 2498.4447 | [5 empty] | Out side air | 253.1058 |  | TOTAL | 218.3955 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 661.4264
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 2.9733
Out side air | 0.12 | 253.1058 | Cfm | 33.6 | 1.08 | 1102.1646 | [5 empty] | Dehumidifed CFM | 748.2552
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 661.4264 | Watts | 3.413 |  | 2257.4484
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 12263.2448 | Room sensible heat - Summer |  |  |  | 13796.1503
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1532.9056 | Room total heat |  |  |  | 16055.3215
Room sensible heat total | [5 empty] | 13796.1503 | Effective sen. heat factor |  |  |  | 0.85929
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 253.1058 | Cfm | 76.2 | 0.68 | 1573.7919 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 748.2552
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 2053.7919
Safety factor |  |  |  |  | 10% | 205.3792
Room latent heat total | [5 empty] | 2259.1711 | AS PER SPECIFICATION - TR |  |  |  | 3
Room total heat | [5 empty] | 16055.3215 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 748.2552
[7 empty] | AS PER DRAWING - TR |  |  |  | 2.9733
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 748.2552
OUT SIDE AIR HEAT
Sensible | 0.88 | 253.1058 | Cfm | 33.6 | 1.08 | 8082.5404
Latent | 0.88 | 253.1058 | Cfm | 76.2 | 0.68 | 11541.1407
Grand total heat ( Btu/hr) | [5 empty] | 35679.0026
Tonnage | [5 empty] | 2.9733
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 3
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 10.6 | 34.768
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.85 | 19.188
Space used for |  | PRIVATE ROOM 3 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 34.768 | 19.188 | 667.1284 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 34.768
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.188
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 667.1284 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 7658.6338 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 81.286 | Glass - E | 0 |  | CFM for people | 22.5
Glass - W |  | 40 | Sq ft | 163 | 0.56 | 3651.2 | No.of Person | 3 |  |  | 0 | Glass- W | 40 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 255.2878 | Glass - S | 0 |  | CFM for Area basis | 40.0277
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 62.5277
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 18.7583
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 180.2782 |  | MIN FA REQT | 81.286
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 180.2782 | Sq ft | 30.6 | 0.34 | 1875.6148 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 40 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 220.2782 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 220.2782 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 40 | Sq ft | 33.6 | 1.13 | 1518.72 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 220.2782 | Sq ft | 28.6 | 0.4 | 2519.9831 | [5 empty] | Out side air | 255.2878 |  | TOTAL | 220.2782 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 667.1284
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.4408
Out side air | 0.12 | 255.2878 | Cfm | 33.6 | 1.08 | 1111.666 | [5 empty] | Dehumidifed CFM | 1042.5876
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3.5
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 667.1284 | Watts | 3.413 |  | 2276.9092
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 17087.0931 | Room sensible heat - Summer |  |  |  | 19222.9797
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 2135.8866 | Room total heat |  |  |  | 21497.0747
Room sensible heat total | [5 empty] | 19222.9797 | Effective sen. heat factor |  |  |  | 0.89421
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 255.2878 | Cfm | 76.2 | 0.68 | 1587.3591 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 1042.5876
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 2067.3591
Safety factor |  |  |  |  | 10% | 206.7359
Room latent heat total | [5 empty] | 2274.095 | AS PER SPECIFICATION - TR |  |  |  | 3.5
Room total heat | [5 empty] | 21497.0747 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 1042.5876
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.4408
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 1042.5876
OUT SIDE AIR HEAT
Sensible | 0.88 | 255.2878 | Cfm | 33.6 | 1.08 | 8152.2175
Latent | 0.88 | 255.2878 | Cfm | 76.2 | 0.68 | 11640.6333
Grand total heat ( Btu/hr) | [5 empty] | 41289.9255
Tonnage | [5 empty] | 3.4408
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 4
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 10.6 | 34.768
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.9 | 19.352
Space used for |  | PRIVATE ROOM 4 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 34.768 | 19.352 | 672.8303 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 34.768
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.352
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 672.8303 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 7724.0923 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 81.7308 | Glass - E | 0 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 257.4697 | Glass - S | 0 |  | CFM for Area basis | 40.3698
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 62.8698
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 18.8609
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 222.161 |  | MIN FA REQT | 81.7308
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 222.161 | Sq ft | 30.6 | 0.34 | 2311.3626 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 451.8528 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 222.161 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 97.9014 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 131.7904 | 0
Partition wall |  | 451.8528 | Sq ft | 28.6 | 0.4 | 5169.196 | [5 empty] | Out side air | 257.4697 |  | TOTAL | 451.8528 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 672.8303
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.2634
Out side air | 0.12 | 257.4697 | Cfm | 33.6 | 1.08 | 1121.1674 | [5 empty] | Dehumidifed CFM | 917.1387
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 672.8303 | Watts | 3.413 |  | 2296.3699
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 15031.096 | Room sensible heat - Summer |  |  |  | 16909.983
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1878.887 | Room total heat |  |  |  | 19199.0019
Room sensible heat total | [5 empty] | 16909.983 | Effective sen. heat factor |  |  |  | 0.88077
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 257.4697 | Cfm | 76.2 | 0.68 | 1600.9263 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 917.1387
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 2080.9263
Safety factor |  |  |  |  | 10% | 208.0926
Room latent heat total | [5 empty] | 2289.0189 | AS PER SPECIFICATION - TR |  |  |  | 3
Room total heat | [5 empty] | 19199.0019 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 917.1387
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.2634
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 917.1387
OUT SIDE AIR HEAT
Sensible | 0.88 | 257.4697 | Cfm | 33.6 | 1.08 | 8221.8946
Latent | 0.88 | 257.4697 | Cfm | 76.2 | 0.68 | 11740.1259
Grand total heat ( Btu/hr) | [5 empty] | 39161.0224
Tonnage | [5 empty] | 3.2634
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 5
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 10.6 | 34.768
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.9 | 19.352
Space used for |  | PRIVATE ROOM 5 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 34.768 | 19.352 | 672.8303 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 34.768
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.352
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 672.8303 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 7724.0923 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 81.7308 | Glass - E | 0 |  | CFM for people | 22.5
Glass - W |  | 20 | Sq ft | 163 | 0.56 | 1825.6 | No.of Person | 3 |  |  | 0 | Glass- W | 20 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 257.4697 | Glass - S | 0 |  | CFM for Area basis | 40.3698
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 62.8698
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 18.8609
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 202.161 |  | MIN FA REQT | 81.7308
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 202.161 | Sq ft | 30.6 | 0.34 | 2103.2826 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 20 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 353.9514 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 222.161 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 20 | Sq ft | 33.6 | 1.13 | 759.36 | [5 empty] | Floor | 0 |  | S | 131.7904 | 0
Partition wall |  | 353.9514 | Sq ft | 28.6 | 0.4 | 4049.2036 | [5 empty] | Out side air | 257.4697 |  | TOTAL | 353.9514 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 672.8303
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.3813
Out side air | 0.12 | 257.4697 | Cfm | 33.6 | 1.08 | 1121.1674 | [5 empty] | Dehumidifed CFM | 993.8291
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3.5
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 672.8303 | Watts | 3.413 |  | 2296.3699
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 16287.9836 | Room sensible heat - Summer |  |  |  | 18323.9815
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 2035.9979 | Room total heat |  |  |  | 20613.0004
Room sensible heat total | [5 empty] | 18323.9815 | Effective sen. heat factor |  |  |  | 0.88895
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 257.4697 | Cfm | 76.2 | 0.68 | 1600.9263 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 993.8291
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 2080.9263
Safety factor |  |  |  |  | 10% | 208.0926
Room latent heat total | [5 empty] | 2289.0189 | AS PER SPECIFICATION - TR |  |  |  | 3.5
Room total heat | [5 empty] | 20613.0004 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 993.8291
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.3813
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 993.8291
OUT SIDE AIR HEAT
Sensible | 0.88 | 257.4697 | Cfm | 33.6 | 1.08 | 8221.8946
Latent | 0.88 | 257.4697 | Cfm | 76.2 | 0.68 | 11740.1259
Grand total heat ( Btu/hr) | [5 empty] | 40575.0208
Tonnage | [5 empty] | 3.3813
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 6
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 10.6 | 34.768
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.9 | 19.352
Space used for |  | PRIVATE ROOM 6 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 34.768 | 19.352 | 672.8303 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 34.768
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.352
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 672.8303 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 7724.0923 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 81.7308 | Glass - E | 0 |  | CFM for people | 22.5
Glass - W |  | 20 | Sq ft | 163 | 0.56 | 1825.6 | No.of Person | 3 |  |  | 0 | Glass- W | 20 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 257.4697 | Glass - S | 0 |  | CFM for Area basis | 40.3698
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 62.8698
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 18.8609
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 202.161 |  | MIN FA REQT | 81.7308
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 202.161 | Sq ft | 30.6 | 0.34 | 2103.2826 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 20 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 753.088 |  | N | 131.7904 | 0
[12 empty] | Partition glass | 0 |  | E | 222.161 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 20 | Sq ft | 33.6 | 1.13 | 759.36 | [5 empty] | Floor | 0 |  | S | 399.1366 | 0
Partition wall |  | 753.088 | Sq ft | 28.6 | 0.4 | 8615.3267 | [5 empty] | Out side air | 257.4697 |  | TOTAL | 753.088 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 672.8303
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.8093
Out side air | 0.12 | 257.4697 | Cfm | 33.6 | 1.08 | 1121.1674 | [5 empty] | Dehumidifed CFM | 1272.436
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 4
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 672.8303 | Watts | 3.413 |  | 2296.3699
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 20854.1067 | Room sensible heat - Summer |  |  |  | 23460.8701
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 2606.7633 | Room total heat |  |  |  | 25749.8889
Room sensible heat total | [5 empty] | 23460.8701 | Effective sen. heat factor |  |  |  | 0.91111
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 257.4697 | Cfm | 76.2 | 0.68 | 1600.9263 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 1272.436
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 2080.9263
Safety factor |  |  |  |  | 10% | 208.0926
Room latent heat total | [5 empty] | 2289.0189 | AS PER SPECIFICATION - TR |  |  |  | 4
Room total heat | [5 empty] | 25749.8889 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 1272.436
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.8093
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 1272.436
OUT SIDE AIR HEAT
Sensible | 0.88 | 257.4697 | Cfm | 33.6 | 1.08 | 8221.8946
Latent | 0.88 | 257.4697 | Cfm | 76.2 | 0.68 | 11740.1259
Grand total heat ( Btu/hr) | [5 empty] | 45711.9094
Tonnage | [5 empty] | 3.8093
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 7
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 9.2 | 30.176
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.9 | 19.352
Space used for |  | PRIVATE ROOM 7 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 30.176 | 19.352 | 583.966 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 30.176
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.352
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 583.966 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 6703.9291 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 40 | Sq ft | 12 | 0.56 | 268.8 | Ventilation air quantity cfm |  |  |  | 74.7993 | Glass - E | 40 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 223.4643 | Glass - S | 0 |  | CFM for Area basis | 35.038
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 57.538
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 182.161 |  | SAFETY 30% | 17.2614
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 74.7993
Wall - E |  | 182.161 | Sq ft | 36.6 | 0.34 | 2266.811 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 40 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 568.5814 |  | N | 346.4205 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 222.161 | 0
All glass |  | 40 | Sq ft | 33.6 | 1.13 | 1518.72 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 568.5814 | Sq ft | 28.6 | 0.4 | 6504.5717 | [5 empty] | Out side air | 223.4643 |  | TOTAL | 568.5814 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 583.966
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.2706
Out side air | 0.12 | 223.4643 | Cfm | 33.6 | 1.08 | 973.0887 | [5 empty] | Dehumidifed CFM | 1077.4262
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 583.966 | Watts | 3.413 |  | 1993.0758
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 17658.0672 | Room sensible heat - Summer |  |  |  | 19865.3256
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 2207.2584 | Room total heat |  |  |  | 21921.7571
Room sensible heat total | [5 empty] | 19865.3256 | Effective sen. heat factor |  |  |  | 0.90619
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 223.4643 | Cfm | 76.2 | 0.68 | 1389.4832 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 1077.4262
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1869.4832
Safety factor |  |  |  |  | 10% | 186.9483
Room latent heat total | [5 empty] | 2056.4315 | AS PER SPECIFICATION - TR |  |  |  | 3
Room total heat | [5 empty] | 21921.7571 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 1077.4262
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.2706
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 1077.4262
OUT SIDE AIR HEAT
Sensible | 0.88 | 223.4643 | Cfm | 33.6 | 1.08 | 7135.984
Latent | 0.88 | 223.4643 | Cfm | 76.2 | 0.68 | 10189.5432
Grand total heat ( Btu/hr) | [5 empty] | 39247.2842
Tonnage | [5 empty] | 3.2706
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 8
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 9.2 | 30.176
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.9 | 19.352
Space used for |  | PRIVATE ROOM 8 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 30.176 | 19.352 | 583.966 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 30.176
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.352
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 583.966 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 6703.9291 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 20 | Sq ft | 12 | 0.56 | 134.4 | Ventilation air quantity cfm |  |  |  | 74.7993 | Glass - E | 20 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 223.4643 | Glass - S | 0 |  | CFM for Area basis | 35.038
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 57.538
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 202.161 |  | SAFETY 30% | 17.2614
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 74.7993
Wall - E |  | 202.161 | Sq ft | 36.6 | 0.34 | 2515.691 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 20 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 395.3712 |  | N | 97.9014 | 0
[12 empty] | Partition glass | 0 |  | E | 75.3088 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 222.161 | 0
All glass |  | 20 | Sq ft | 33.6 | 1.13 | 759.36 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 395.3712 | Sq ft | 28.6 | 0.4 | 4523.0465 | [5 empty] | Out side air | 223.4643 |  | TOTAL | 395.3712 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 583.966
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.0244
Out side air | 0.12 | 223.4643 | Cfm | 33.6 | 1.08 | 973.0887 | [5 empty] | Dehumidifed CFM | 917.1732
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 583.966 | Watts | 3.413 |  | 1993.0758
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 15031.662 | Room sensible heat - Summer |  |  |  | 16910.6198
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1878.9578 | Room total heat |  |  |  | 18967.0513
Room sensible heat total | [5 empty] | 16910.6198 | Effective sen. heat factor |  |  |  | 0.89158
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 223.4643 | Cfm | 76.2 | 0.68 | 1389.4832 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 917.1732
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1869.4832
Safety factor |  |  |  |  | 10% | 186.9483
Room latent heat total | [5 empty] | 2056.4315 | AS PER SPECIFICATION - TR |  |  |  | 3
Room total heat | [5 empty] | 18967.0513 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 917.1732
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.0244
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 917.1732
OUT SIDE AIR HEAT
Sensible | 0.88 | 223.4643 | Cfm | 33.6 | 1.08 | 7135.984
Latent | 0.88 | 223.4643 | Cfm | 76.2 | 0.68 | 10189.5432
Grand total heat ( Btu/hr) | [5 empty] | 36292.5784
Tonnage | [5 empty] | 3.0244
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 9
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 9.2 | 30.176
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.9 | 19.352
Space used for |  | PRIVATE ROOM 9 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 30.176 | 19.352 | 583.966 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 30.176
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.352
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 583.966 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 6703.9291 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 40 | Sq ft | 12 | 0.56 | 268.8 | Ventilation air quantity cfm |  |  |  | 74.7993 | Glass - E | 40 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 223.4643 | Glass - S | 0 |  | CFM for Area basis | 35.038
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 57.538
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 182.161 |  | SAFETY 30% | 17.2614
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 74.7993
Wall - E |  | 182.161 | Sq ft | 36.6 | 0.34 | 2266.811 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 40 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 395.3712 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 75.3088 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 222.161 | 0
All glass |  | 40 | Sq ft | 33.6 | 1.13 | 1518.72 | [5 empty] | Floor | 0 |  | S | 97.9014 | 0
Partition wall |  | 395.3712 | Sq ft | 28.6 | 0.4 | 4523.0465 | [5 empty] | Out side air | 223.4643 |  | TOTAL | 395.3712 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 583.966
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.0848
Out side air | 0.12 | 223.4643 | Cfm | 33.6 | 1.08 | 973.0887 | [5 empty] | Dehumidifed CFM | 956.5213
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 583.966 | Watts | 3.413 |  | 1993.0758
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 15676.542 | Room sensible heat - Summer |  |  |  | 17636.1098
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1959.5678 | Room total heat |  |  |  | 19692.5413
Room sensible heat total | [5 empty] | 17636.1098 | Effective sen. heat factor |  |  |  | 0.89557
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 223.4643 | Cfm | 76.2 | 0.68 | 1389.4832 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 956.5213
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1869.4832
Safety factor |  |  |  |  | 10% | 186.9483
Room latent heat total | [5 empty] | 2056.4315 | AS PER SPECIFICATION - TR |  |  |  | 3
Room total heat | [5 empty] | 19692.5413 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 956.5213
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.0848
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 956.5213
OUT SIDE AIR HEAT
Sensible | 0.88 | 223.4643 | Cfm | 33.6 | 1.08 | 7135.984
Latent | 0.88 | 223.4643 | Cfm | 76.2 | 0.68 | 10189.5432
Grand total heat ( Btu/hr) | [5 empty] | 37018.0684
Tonnage | [5 empty] | 3.0848
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 10
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 9.2 | 30.176
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.6 | 18.368
Space used for |  | PRIVATE ROOM 10 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 30.176 | 18.368 | 554.2728 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 30.176
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 18.368
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 554.2728 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 6363.0514 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 20 | Sq ft | 12 | 0.56 | 134.4 | Ventilation air quantity cfm |  |  |  | 72.4833 | Glass - E | 20 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 212.1017 | Glass - S | 0 |  | CFM for Area basis | 33.2564
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 55.7564
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 190.8646 |  | SAFETY 30% | 16.7269
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 72.4833
Wall - E |  | 190.8646 | Sq ft | 36.6 | 0.34 | 2375.1196 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 20 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 384.0749 |  | N | 97.9014 | 0
[12 empty] | Partition glass | 0 |  | E | 75.3088 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 210.8646 | 0
All glass |  | 20 | Sq ft | 33.6 | 1.13 | 759.36 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 384.0749 | Sq ft | 28.6 | 0.4 | 4393.8166 | [5 empty] | Out side air | 212.1017 |  | TOTAL | 384.0749 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 554.2728
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 2.9051
Out side air | 0.12 | 212.1017 | Cfm | 33.6 | 1.08 | 923.6096 | [5 empty] | Dehumidifed CFM | 891.5084
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 554.2728 | Watts | 3.413 |  | 1891.733
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 14611.0388 | Room sensible heat - Summer |  |  |  | 16437.4186
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1826.3798 | Room total heat |  |  |  | 18416.1333
Room sensible heat total | [5 empty] | 16437.4186 | Effective sen. heat factor |  |  |  | 0.89256
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 212.1017 | Cfm | 76.2 | 0.68 | 1318.8315 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 891.5084
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1798.8315
Safety factor |  |  |  |  | 10% | 179.8831
Room latent heat total | [5 empty] | 1978.7146 | AS PER SPECIFICATION - TR |  |  |  | 3
Room total heat | [5 empty] | 18416.1333 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 891.5084
[7 empty] | AS PER DRAWING - TR |  |  |  | 2.9051
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 891.5084
OUT SIDE AIR HEAT
Sensible | 0.88 | 212.1017 | Cfm | 33.6 | 1.08 | 6773.1373
Latent | 0.88 | 212.1017 | Cfm | 76.2 | 0.68 | 9671.4309
Grand total heat ( Btu/hr) | [5 empty] | 34860.7014
Tonnage | [5 empty] | 2.9051
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 11
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 9.2 | 30.176
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.9 | 19.352
Space used for |  | PRIVATE ROOM 11 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 30.176 | 19.352 | 583.966 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 30.176
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.352
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 583.966 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 6703.9291 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 20 | Sq ft | 12 | 0.56 | 134.4 | Ventilation air quantity cfm |  |  |  | 74.7993 | Glass - E | 20 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 223.4643 | Glass - S | 0 |  | CFM for Area basis | 35.038
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 57.538
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 202.161 |  | SAFETY 30% | 17.2614
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 74.7993
Wall - E |  | 202.161 | Sq ft | 36.6 | 0.34 | 2515.691 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 20 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 395.3712 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 75.3088 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 222.161 | 0
All glass |  | 20 | Sq ft | 33.6 | 1.13 | 759.36 | [5 empty] | Floor | 0 |  | S | 97.9014 | 0
Partition wall |  | 395.3712 | Sq ft | 28.6 | 0.4 | 4523.0465 | [5 empty] | Out side air | 223.4643 |  | TOTAL | 395.3712 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 583.966
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.0244
Out side air | 0.12 | 223.4643 | Cfm | 33.6 | 1.08 | 973.0887 | [5 empty] | Dehumidifed CFM | 917.1732
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 583.966 | Watts | 3.413 |  | 1993.0758
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 15031.662 | Room sensible heat - Summer |  |  |  | 16910.6198
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1878.9578 | Room total heat |  |  |  | 18967.0513
Room sensible heat total | [5 empty] | 16910.6198 | Effective sen. heat factor |  |  |  | 0.89158
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 223.4643 | Cfm | 76.2 | 0.68 | 1389.4832 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 917.1732
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1869.4832
Safety factor |  |  |  |  | 10% | 186.9483
Room latent heat total | [5 empty] | 2056.4315 | AS PER SPECIFICATION - TR |  |  |  | 3
Room total heat | [5 empty] | 18967.0513 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 917.1732
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.0244
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 917.1732
OUT SIDE AIR HEAT
Sensible | 0.88 | 223.4643 | Cfm | 33.6 | 1.08 | 7135.984
Latent | 0.88 | 223.4643 | Cfm | 76.2 | 0.68 | 10189.5432
Grand total heat ( Btu/hr) | [5 empty] | 36292.5784
Tonnage | [5 empty] | 3.0244
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 12
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 9.2 | 30.176
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.9 | 19.352
Space used for |  | PRIVATE ROOM 12 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 30.176 | 19.352 | 583.966 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 30.176
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.352
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 583.966 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 6703.9291 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 20 | Sq ft | 12 | 0.56 | 134.4 | Ventilation air quantity cfm |  |  |  | 74.7993 | Glass - E | 20 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 223.4643 | Glass - S | 0 |  | CFM for Area basis | 35.038
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 57.538
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 202.161 |  | SAFETY 30% | 17.2614
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 74.7993
Wall - E |  | 202.161 | Sq ft | 36.6 | 0.34 | 2515.691 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 20 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 395.3712 |  | N | 97.9014 | 0
[12 empty] | Partition glass | 0 |  | E | 75.3088 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 222.161 | 0
All glass |  | 20 | Sq ft | 33.6 | 1.13 | 759.36 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 395.3712 | Sq ft | 28.6 | 0.4 | 4523.0465 | [5 empty] | Out side air | 223.4643 |  | TOTAL | 395.3712 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 583.966
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.0244
Out side air | 0.12 | 223.4643 | Cfm | 33.6 | 1.08 | 973.0887 | [5 empty] | Dehumidifed CFM | 917.1732
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 583.966 | Watts | 3.413 |  | 1993.0758
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 15031.662 | Room sensible heat - Summer |  |  |  | 16910.6198
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1878.9578 | Room total heat |  |  |  | 18967.0513
Room sensible heat total | [5 empty] | 16910.6198 | Effective sen. heat factor |  |  |  | 0.89158
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 223.4643 | Cfm | 76.2 | 0.68 | 1389.4832 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 917.1732
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1869.4832
Safety factor |  |  |  |  | 10% | 186.9483
Room latent heat total | [5 empty] | 2056.4315 | AS PER SPECIFICATION - TR |  |  |  | 3
Room total heat | [5 empty] | 18967.0513 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 917.1732
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.0244
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 917.1732
OUT SIDE AIR HEAT
Sensible | 0.88 | 223.4643 | Cfm | 33.6 | 1.08 | 7135.984
Latent | 0.88 | 223.4643 | Cfm | 76.2 | 0.68 | 10189.5432
Grand total heat ( Btu/hr) | [5 empty] | 36292.5784
Tonnage | [5 empty] | 3.0244
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 13
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 9.2 | 30.176
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.9 | 19.352
Space used for |  | PRIVATE ROOM 13 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 30.176 | 19.352 | 583.966 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 30.176
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.352
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 583.966 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 6703.9291 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 20 | Sq ft | 12 | 0.56 | 134.4 | Ventilation air quantity cfm |  |  |  | 74.7993 | Glass - E | 20 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 223.4643 | Glass - S | 0 |  | CFM for Area basis | 35.038
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 57.538
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 202.161 |  | SAFETY 30% | 17.2614
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 74.7993
Wall - E |  | 202.161 | Sq ft | 36.6 | 0.34 | 2515.691 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 20 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 395.3712 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 75.3088 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 222.161 | 0
All glass |  | 20 | Sq ft | 33.6 | 1.13 | 759.36 | [5 empty] | Floor | 0 |  | S | 97.9014 | 0
Partition wall |  | 395.3712 | Sq ft | 28.6 | 0.4 | 4523.0465 | [5 empty] | Out side air | 223.4643 |  | TOTAL | 395.3712 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 583.966
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.0244
Out side air | 0.12 | 223.4643 | Cfm | 33.6 | 1.08 | 973.0887 | [5 empty] | Dehumidifed CFM | 917.1732
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 583.966 | Watts | 3.413 |  | 1993.0758
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 15031.662 | Room sensible heat - Summer |  |  |  | 16910.6198
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1878.9578 | Room total heat |  |  |  | 18967.0513
Room sensible heat total | [5 empty] | 16910.6198 | Effective sen. heat factor |  |  |  | 0.89158
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 223.4643 | Cfm | 76.2 | 0.68 | 1389.4832 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 917.1732
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1869.4832
Safety factor |  |  |  |  | 10% | 186.9483
Room latent heat total | [5 empty] | 2056.4315 | AS PER SPECIFICATION - TR |  |  |  | 3
Room total heat | [5 empty] | 18967.0513 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 917.1732
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.0244
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 917.1732
OUT SIDE AIR HEAT
Sensible | 0.88 | 223.4643 | Cfm | 33.6 | 1.08 | 7135.984
Latent | 0.88 | 223.4643 | Cfm | 76.2 | 0.68 | 10189.5432
Grand total heat ( Btu/hr) | [5 empty] | 36292.5784
Tonnage | [5 empty] | 3.0244
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## PRIVATE ROOM 14
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 9.2 | 30.176
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.9 | 19.352
Space used for |  | PRIVATE ROOM 14 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 30.176 | 19.352 | 583.966 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 30.176
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.352
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 583.966 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 6703.9291 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 2 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 20 | Sq ft | 12 | 0.56 | 134.4 | Ventilation air quantity cfm |  |  |  | 74.7993 | Glass - E | 20 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 60 | Sq ft | 12 | 0.56 | 403.2 | With Air change Vent Air CFM Reqd |  |  |  | 223.4643 | Glass - S | 60 |  | CFM for Area basis | 35.038
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 57.538
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 202.161 |  | SAFETY 30% | 17.2614
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 74.7993
Wall - E |  | 202.161 | Sq ft | 36.6 | 0.34 | 2515.691 | [5 empty] | Wall - S | 286.4205
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 286.4205 | Sq ft | 34.6 | 0.34 | 3369.4505 | [5 empty] | All glass | 80 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 395.3712 |  | N | 97.9014 | 0
[12 empty] | Partition glass | 0 |  | E | 75.3088 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 222.161 | 0
All glass |  | 80 | Sq ft | 33.6 | 1.13 | 3037.44 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 395.3712 | Sq ft | 28.6 | 0.4 | 4523.0465 | [5 empty] | Out side air | 223.4643 |  | TOTAL | 395.3712 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 583.966
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.5916
Out side air | 0.12 | 223.4643 | Cfm | 33.6 | 1.08 | 973.0887 | [5 empty] | Dehumidifed CFM | 1286.3651
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3.5
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 583.966 | Watts | 3.413 |  | 1993.0758
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 21082.3926 | Room sensible heat - Summer |  |  |  | 23717.6916
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 2635.2991 | Room total heat |  |  |  | 25774.1231
Room sensible heat total | [5 empty] | 23717.6916 | Effective sen. heat factor |  |  |  | 0.92021
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 223.4643 | Cfm | 76.2 | 0.68 | 1389.4832 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 1286.3651
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1869.4832
Safety factor |  |  |  |  | 10% | 186.9483
Room latent heat total | [5 empty] | 2056.4315 | AS PER SPECIFICATION - TR |  |  |  | 3.5
Room total heat | [5 empty] | 25774.1231 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 1286.3651
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.5916
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 1286.3651
OUT SIDE AIR HEAT
Sensible | 0.88 | 223.4643 | Cfm | 33.6 | 1.08 | 7135.984
Latent | 0.88 | 223.4643 | Cfm | 76.2 | 0.68 | 10189.5432
Grand total heat ( Btu/hr) | [5 empty] | 43099.6503
Tonnage | [5 empty] | 3.5916
NOTE:
THE FLOOR ABOVE & BELOW THE CONDITION SPACE ARE ASSUMED TO BE AIR CONDITIONED

## COLD STORAGE
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 3.5 | 11.48
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 3 | 9.84
Space used for |  | COLD STORAGE |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 11.48 | 9.84 | 112.9632 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 11.48
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.84
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 112.9632 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 1296.8175 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 38.0611 | Glass - E | 0 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 6.7778
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 29.2778
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 8.7833
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 38.0611
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 112.9632
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 112.9632 | Sq ft | 53.6 | 0.4 | 2421.931 | [5 empty] | Partition wall | 357.7168 |  | N | 131.7904 | 0
[12 empty] | Partition glass | 0 |  | E | 112.9632 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 112.9632 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 357.7168 | Sq ft | 28.6 | 0.4 | 4092.2802 | [5 empty] | Out side air | 38.0611 |  | TOTAL | 357.7168 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 2
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 112.9632
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.6814
Out side air | 0.12 | 38.0611 | Cfm | 33.6 | 1.08 | 165.7395 | [5 empty] | Dehumidifed CFM | 891.5362
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 2
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 2 | KW | 3413 | 1 | 6826
Lights |  | 112.9632 | Watts | 3.413 |  | 385.5434
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 14611.4941 | Room sensible heat - Summer |  |  |  | 16437.9308
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1826.4368 | Room total heat |  |  |  | 17226.258
Room sensible heat total | [5 empty] | 16437.9308 | Effective sen. heat factor |  |  |  | 0.95424
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 38.0611 | Cfm | 76.2 | 0.68 | 236.6611 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 891.5362
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 716.6611
Safety factor |  |  |  |  | 10% | 71.6661
Room latent heat total | [5 empty] | 788.3272 | AS PER SPECIFICATION - TR |  |  |  | 2
Room total heat | [5 empty] | 17226.258 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 891.5362
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.6814
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 891.5362
OUT SIDE AIR HEAT
Sensible | 0.88 | 38.0611 | Cfm | 33.6 | 1.08 | 1215.4228
Latent | 0.88 | 38.0611 | Cfm | 76.2 | 0.68 | 1735.5144
Grand total heat ( Btu/hr) | [5 empty] | 20177.1952
Tonnage | [5 empty] | 1.6814
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## PREPARATION ROOM
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 5.8 | 19.024
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.5 | 18.04
Space used for |  | PREPARATION ROOM |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 19.024 | 18.04 | 343.193 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 19.024
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 18.04
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 343.193 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 3939.8552 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 65.7691 | Glass - E | 0 |  | CFM for people | 30
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 4 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 20.5916
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 50.5916
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 15.1775
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 65.7691
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 343.193
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 343.193 | Sq ft | 53.6 | 0.4 | 7358.0571 | [5 empty] | Partition wall | 512.0998 |  | N | 75.3088 | 0
[12 empty] | Partition glass | 0 |  | E | 218.3955 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 218.3955 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 512.0998 | Sq ft | 28.6 | 0.4 | 5858.4222 | [5 empty] | Out side air | 65.7691 |  | TOTAL | 512.0998 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 4
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 343.193
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 2.1468
Out side air | 0.12 | 65.7691 | Cfm | 33.6 | 1.08 | 286.3953 | [5 empty] | Dehumidifed CFM | 1058.0612
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 2
People |  | 4 | Nos | 240 |  | 960
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 343.193 | Watts | 3.413 |  | 1171.3176
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 17340.6921 | Room sensible heat - Summer |  |  |  | 19508.2786
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 2167.5865 | Room total heat |  |  |  | 20662.12
Room sensible heat total | [5 empty] | 19508.2786 | Effective sen. heat factor |  |  |  | 0.94416
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 65.7691 | Cfm | 76.2 | 0.68 | 408.9467 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 4 | Nos | 160 |  | 640 | Dehumidifed CFM |  |  |  | 1058.0612
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1048.9467
Safety factor |  |  |  |  | 10% | 104.8947
Room latent heat total | [5 empty] | 1153.8414 | AS PER SPECIFICATION - TR |  |  |  | 2
Room total heat | [5 empty] | 20662.12 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 1058.0612
[7 empty] | AS PER DRAWING - TR |  |  |  | 2.1468
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 1058.0612
OUT SIDE AIR HEAT
Sensible | 0.88 | 65.7691 | Cfm | 33.6 | 1.08 | 2100.232
Latent | 0.88 | 65.7691 | Cfm | 76.2 | 0.68 | 2998.9424
Grand total heat ( Btu/hr) | [5 empty] | 25761.2944
Tonnage | [5 empty] | 2.1468
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## DISINFECTION AIRLOCK
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 5.8 | 19.024
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 3 | 9.84
Space used for |  | DISINFECTION AIRLOCK |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 19.024 | 9.84 | 187.1962 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 19.024
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.84
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 187.1962 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 2149.0119 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 34.1013 | Glass - E | 0 |  | CFM for people | 15
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 2 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 11.2318
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 26.2318
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 7.8695
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 34.1013
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 187.1962
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 187.1962 | Sq ft | 53.6 | 0.4 | 4013.4857 | [5 empty] | Partition wall | 549.7542 |  | N | 112.9632 | 0
[12 empty] | Partition glass | 0 |  | E | 218.3955 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 218.3955 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 549.7542 | Sq ft | 28.6 | 0.4 | 6289.1885 | [5 empty] | Out side air | 34.1013 |  | TOTAL | 549.7542 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 2
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.2
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 187.1962
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.4178
Out side air | 0.12 | 34.1013 | Cfm | 33.6 | 1.08 | 148.4962 | [5 empty] | Dehumidifed CFM | 747.6101
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1.5
People |  | 2 | Nos | 240 |  | 480
Equipment |  | 0.2 | KW | 3413 | 1 | 682.6
Lights |  | 187.1962 | Watts | 3.413 |  | 638.9005
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 12252.6708 | Room sensible heat - Summer |  |  |  | 13784.2547
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1531.5839 | Room total heat |  |  |  | 14369.4978
Room sensible heat total | [5 empty] | 13784.2547 | Effective sen. heat factor |  |  |  | 0.95927
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 34.1013 | Cfm | 76.2 | 0.68 | 212.0392 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 2 | Nos | 160 |  | 320 | Dehumidifed CFM |  |  |  | 747.6101
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 532.0392
Safety factor |  |  |  |  | 10% | 53.2039
Room latent heat total | [5 empty] | 585.2431 | AS PER SPECIFICATION - TR |  |  |  | 1.5
Room total heat | [5 empty] | 14369.4978 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 747.6101
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.4178
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 747.6101
OUT SIDE AIR HEAT
Sensible | 0.88 | 34.1013 | Cfm | 33.6 | 1.08 | 1088.9718
Latent | 0.88 | 34.1013 | Cfm | 76.2 | 0.68 | 1554.9538
Grand total heat ( Btu/hr) | [5 empty] | 17013.4234
Tonnage | [5 empty] | 1.4178
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## PRE PCR
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 6.8 | 22.304
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.9 | 19.352
Space used for |  | PRE PCR |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 22.304 | 19.352 | 431.627 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 22.304
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.352
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 431.627 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 4955.0781 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 66.1669 | Glass - E | 0 |  | CFM for people | 25
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 5 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 25.8976
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 50.8976
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 15.2693
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 66.1669
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 431.627
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 431.627 | Sq ft | 53.6 | 0.4 | 9254.0831 | [5 empty] | Partition wall | 267.3462 |  | N | 45.1853 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 222.161 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 267.3462 | Sq ft | 28.6 | 0.4 | 3058.441 | [5 empty] | Out side air | 66.1669 |  | TOTAL | 267.3462 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 5
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 2
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 431.627
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 2.6104
Out side air | 0.12 | 66.1669 | Cfm | 33.6 | 1.08 | 288.1278 | [5 empty] | Dehumidifed CFM | 1348.443
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 2.5
People |  | 5 | Nos | 240 |  | 1200
Equipment |  | 2 | KW | 3413 | 1 | 6826
Lights |  | 431.627 | Watts | 3.413 |  | 1473.143
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 22099.7948 | Room sensible heat - Summer |  |  |  | 24862.2691
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 2762.4743 | Room total heat |  |  |  | 26194.8317
Room sensible heat total | [5 empty] | 24862.2691 | Effective sen. heat factor |  |  |  | 0.94913
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 66.1669 | Cfm | 76.2 | 0.68 | 411.4205 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 5 | Nos | 160 |  | 800 | Dehumidifed CFM |  |  |  | 1348.443
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1211.4205
Safety factor |  |  |  |  | 10% | 121.1421
Room latent heat total | [5 empty] | 1332.5626 | AS PER SPECIFICATION - TR |  |  |  | 2.5
Room total heat | [5 empty] | 26194.8317 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 1348.443
[7 empty] | AS PER DRAWING - TR |  |  |  | 2.6104
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 1348.443
OUT SIDE AIR HEAT
Sensible | 0.88 | 66.1669 | Cfm | 33.6 | 1.08 | 2112.9369
Latent | 0.88 | 66.1669 | Cfm | 76.2 | 0.68 | 3017.0839
Grand total heat ( Btu/hr) | [5 empty] | 31324.8526
Tonnage | [5 empty] | 2.6104
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## PCR ASSAY ROOM
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 6.6 | 21.648
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 5.9 | 19.352
Space used for |  | PCR ASSAY ROOM |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 21.648 | 19.352 | 418.9321 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 21.648
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.352
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 418.9321 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 4809.3405 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 65.1767 | Glass - E | 0 |  | CFM for people | 25
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 5 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 25.1359
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 50.1359
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 15.0408
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 65.1767
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 418.9321
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 418.9321 | Sq ft | 53.6 | 0.4 | 8981.9041 | [5 empty] | Partition wall | 75.3088 |  | N | 75.3088 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 75.3088 | Sq ft | 28.6 | 0.4 | 861.5327 | [5 empty] | Out side air | 65.1767 |  | TOTAL | 75.3088 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 5
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 2
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 418.9321
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 2.3675
Out side air | 0.12 | 65.1767 | Cfm | 33.6 | 1.08 | 283.8159 | [5 empty] | Dehumidifed CFM | 1194.8822
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 2.5
People |  | 5 | Nos | 240 |  | 1200
Equipment |  | 2 | KW | 3413 | 1 | 6826
Lights |  | 418.9321 | Watts | 3.413 |  | 1429.8152
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 19583.0679 | Room sensible heat - Summer |  |  |  | 22030.9514
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 2447.8835 | Room total heat |  |  |  | 23356.7413
Room sensible heat total | [5 empty] | 22030.9514 | Effective sen. heat factor |  |  |  | 0.94324
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 65.1767 | Cfm | 76.2 | 0.68 | 405.2635 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 5 | Nos | 160 |  | 800 | Dehumidifed CFM |  |  |  | 1194.8822
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1205.2635
Safety factor |  |  |  |  | 10% | 120.5264
Room latent heat total | [5 empty] | 1325.7899 | AS PER SPECIFICATION - TR |  |  |  | 2.5
Room total heat | [5 empty] | 23356.7413 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 1194.8822
[7 empty] | AS PER DRAWING - TR |  |  |  | 2.3675
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 1194.8822
OUT SIDE AIR HEAT
Sensible | 0.88 | 65.1767 | Cfm | 33.6 | 1.08 | 2081.3164
Latent | 0.88 | 65.1767 | Cfm | 76.2 | 0.68 | 2971.9325
Grand total heat ( Btu/hr) | [5 empty] | 28409.9902
Tonnage | [5 empty] | 2.3675
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## POST PCR
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 7 | 22.96
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 6.1 | 20.008
Space used for |  | POST PCR |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 22.96 | 20.008 | 459.3837 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 22.96
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 20.008
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 459.3837 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 5273.7246 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 40 | Sq ft | 12 | 0.56 | 268.8 | Ventilation air quantity cfm |  |  |  | 68.3319 | Glass - E | 40 |  | CFM for people | 25
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 5 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 27.563
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 52.563
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 189.6918 |  | SAFETY 30% | 15.7689
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 68.3319
Wall - E |  | 189.6918 | Sq ft | 36.6 | 0.34 | 2360.5253 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 459.3837
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 40 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 459.3837 | Sq ft | 53.6 | 0.4 | 9849.1861 | [5 empty] | Partition wall | 263.5808 |  | N | 263.5808 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 40 | Sq ft | 33.6 | 1.13 | 1518.72 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 263.5808 | Sq ft | 28.6 | 0.4 | 3015.3644 | [5 empty] | Out side air | 68.3319 |  | TOTAL | 263.5808 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 5
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 2
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 459.3837
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 3.076
Out side air | 0.12 | 68.3319 | Cfm | 33.6 | 1.08 | 297.5555 | [5 empty] | Dehumidifed CFM | 1641.5785
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 3.5
People |  | 5 | Nos | 240 |  | 1200
Equipment |  | 2 | KW | 3413 | 1 | 6826
Lights |  | 459.3837 | Watts | 3.413 |  | 1567.8765
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 26904.0277 | Room sensible heat - Summer |  |  |  | 30267.0311
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 3363.0035 | Room total heat |  |  |  | 31614.4018
Room sensible heat total | [5 empty] | 30267.0311 | Effective sen. heat factor |  |  |  | 0.95738
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 68.3319 | Cfm | 76.2 | 0.68 | 424.8825 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 5 | Nos | 160 |  | 800 | Dehumidifed CFM |  |  |  | 1641.5785
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1224.8825
Safety factor |  |  |  |  | 10% | 122.4882
Room latent heat total | [5 empty] | 1347.3707 | AS PER SPECIFICATION - TR |  |  |  | 3.5
Room total heat | [5 empty] | 31614.4018 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 1641.5785
[7 empty] | AS PER DRAWING - TR |  |  |  | 3.076
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 1641.5785
OUT SIDE AIR HEAT
Sensible | 0.88 | 68.3319 | Cfm | 33.6 | 1.08 | 2182.0735
Latent | 0.88 | 68.3319 | Cfm | 76.2 | 0.68 | 3115.8047
Grand total heat ( Btu/hr) | [5 empty] | 36912.28
Tonnage | [5 empty] | 3.076
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## SKILL DEVELOPMENT LAB
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 22.3 | 73.144
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 6.6 | 21.648
Space used for |  | SKILL DEVELOPMENT LAB |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 73.144 | 21.648 | 1583.4213 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 73.144
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 21.648
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 1583.4213 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 18177.6767 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 20 | Sq ft | 12 | 0.56 | 134.4 | Ventilation air quantity cfm |  |  |  | 318.5069 | Glass - E | 20 |  | CFM for people | 150
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 20 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 95.0053
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 245.0053
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 55.3088 |  | SAFETY 30% | 73.5016
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 318.5069
Wall - E |  | 55.3088 | Sq ft | 36.6 | 0.34 | 688.2627 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 0
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 20 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 0 | Sq ft | 53.6 | 0.4 | 0 | [5 empty] | Partition wall | 402.9021 |  | N | 214.6301 | 0
[12 empty] | Partition glass | 20 |  | E | 0 | 20
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 188.272 | 0
All glass |  | 20 | Sq ft | 33.6 | 1.13 | 759.36 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 402.9021 | Sq ft | 28.6 | 0.4 | 4609.1998 | [5 empty] | Out side air | 318.5069 |  | TOTAL | 402.9021 | 20
Partition glass |  | 20 | Sq ft | 28.6 | 1.1 | 629.2 | [5 empty] | People | 20
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 2
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 1583.4213
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 4.8988
Out side air | 0.12 | 318.5069 | Cfm | 33.6 | 1.08 | 1386.9572 | [5 empty] | Dehumidifed CFM | 1539.8994
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 5
People |  | 20 | Nos | 240 |  | 4800
Equipment |  | 2 | KW | 3413 | 1 | 6826
Lights |  | 1583.4213 | Watts | 3.413 |  | 5404.2169
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 25237.5967 | Room sensible heat - Summer |  |  |  | 28392.2963
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 3154.6996 | Room total heat |  |  |  | 34090.7915
Room sensible heat total | [5 empty] | 28392.2963 | Effective sen. heat factor |  |  |  | 0.83284
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 318.5069 | Cfm | 76.2 | 0.68 | 1980.4502 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 20 | Nos | 160 |  | 3200 | Dehumidifed CFM |  |  |  | 1539.8994
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 5180.4502
Safety factor |  |  |  |  | 10% | 518.045
Room latent heat total | [5 empty] | 5698.4952 | AS PER SPECIFICATION - TR |  |  |  | 5
Room total heat | [5 empty] | 34090.7915 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 1539.8994
[7 empty] | AS PER DRAWING - TR |  |  |  | 4.8988
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 1539.8994
OUT SIDE AIR HEAT
Sensible | 0.88 | 318.5069 | Cfm | 33.6 | 1.08 | 10171.0198
Latent | 0.88 | 318.5069 | Cfm | 76.2 | 0.68 | 14523.3014
Grand total heat ( Btu/hr) | [5 empty] | 58785.1126
Tonnage | [5 empty] | 4.8988
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## ROOM 1
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 3.5 | 11.48
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 4.9 | 16.072
Space used for |  | ROOM 1 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 11.48 | 16.072 | 184.5066 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 11.48
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 16.072
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 184.5066 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 2118.1353 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 33.8915 | Glass - E | 0 |  | CFM for people | 15
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 11.0704
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 26.0704
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 7.8211
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 33.8915
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 184.5066
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 184.5066 | Sq ft | 53.6 | 0.4 | 3955.8206 | [5 empty] | Partition wall | 184.5066 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 184.5066 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 184.5066 | Sq ft | 28.6 | 0.4 | 2110.755 | [5 empty] | Out side air | 33.8915 |  | TOTAL | 184.5066 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 184.5066
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.1514
Out side air | 0.12 | 33.8915 | Cfm | 33.6 | 1.08 | 147.5826 | [5 empty] | Dehumidifed CFM | 565.6423
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 184.5066 | Watts | 3.413 |  | 629.7209
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 9270.3792 | Room sensible heat - Summer |  |  |  | 10429.1766
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1158.7974 | Room total heat |  |  |  | 11188.9848
Room sensible heat total | [5 empty] | 10429.1766 | Effective sen. heat factor |  |  |  | 0.93209
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 33.8915 | Cfm | 76.2 | 0.68 | 210.7347 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 565.6423
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 690.7347
Safety factor |  |  |  |  | 10% | 69.0735
Room latent heat total | [5 empty] | 759.8082 | AS PER SPECIFICATION - TR |  |  |  | 1
Room total heat | [5 empty] | 11188.9848 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 565.6423
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.1514
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 565.6423
OUT SIDE AIR HEAT
Sensible | 0.88 | 33.8915 | Cfm | 33.6 | 1.08 | 1082.2726
Latent | 0.88 | 33.8915 | Cfm | 76.2 | 0.68 | 1545.3879
Grand total heat ( Btu/hr) | [5 empty] | 13816.6452
Tonnage | [5 empty] | 1.1514
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## ROOM 2
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 3.5 | 11.48
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 2.9 | 9.512
Space used for |  | ROOM 2 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 11.48 | 9.512 | 109.1978 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 11.48
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.512
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 109.1978 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 1253.5903 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 28.0174 | Glass - E | 0 |  | CFM for people | 15
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 6.5519
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 21.5519
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 6.4656
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 28.0174
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 109.1978
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 109.1978 | Sq ft | 53.6 | 0.4 | 2341.2 | [5 empty] | Partition wall | 0 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 0 | Sq ft | 28.6 | 0.4 | 0 | [5 empty] | Out side air | 28.0174 |  | TOTAL | 0 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 109.1978
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 0.73434
Out side air | 0.12 | 28.0174 | Cfm | 33.6 | 1.08 | 122.0036 | [5 empty] | Dehumidifed CFM | 321.0908
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 109.1978 | Watts | 3.413 |  | 372.692
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 5262.3955 | Room sensible heat - Summer |  |  |  | 5920.1949
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 657.7994 | Room total heat |  |  |  | 6639.826
Room sensible heat total | [5 empty] | 5920.1949 | Effective sen. heat factor |  |  |  | 0.89162
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 28.0174 | Cfm | 76.2 | 0.68 | 174.2101 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 321.0908
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 654.2101
Safety factor |  |  |  |  | 10% | 65.421
Room latent heat total | [5 empty] | 719.6311 | AS PER SPECIFICATION - TR |  |  |  | 1
Room total heat | [5 empty] | 6639.826 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 321.0908
[7 empty] | AS PER DRAWING - TR |  |  |  | 0.73434
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 321.0908
OUT SIDE AIR HEAT
Sensible | 0.88 | 28.0174 | Cfm | 33.6 | 1.08 | 894.6928
Latent | 0.88 | 28.0174 | Cfm | 76.2 | 0.68 | 1277.5408
Grand total heat ( Btu/hr) | [5 empty] | 8812.0596
Tonnage | [5 empty] | 0.73434
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## ROOM 3
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 3.5 | 11.48
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 2.9 | 9.512
Space used for |  | ROOM 3 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 11.48 | 9.512 | 109.1978 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 11.48
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.512
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 109.1978 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 1253.5903 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 37.7674 | Glass - E | 0 |  | CFM for people | 22.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 6.5519
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 29.0519
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 8.7156
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 37.7674
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 109.1978
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 109.1978 | Sq ft | 53.6 | 0.4 | 2341.2 | [5 empty] | Partition wall | 0 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 0 | Sq ft | 28.6 | 0.4 | 0 | [5 empty] | Out side air | 37.7674 |  | TOTAL | 0 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 109.1978
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 0.80687
Out side air | 0.12 | 37.7674 | Cfm | 33.6 | 1.08 | 164.4605 | [5 empty] | Dehumidifed CFM | 323.6813
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 0.5
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 109.1978 | Watts | 3.413 |  | 372.692
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 5304.8524 | Room sensible heat - Summer |  |  |  | 5967.959
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 663.1066 | Room total heat |  |  |  | 6754.2773
Room sensible heat total | [5 empty] | 5967.959 | Effective sen. heat factor |  |  |  | 0.88358
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 37.7674 | Cfm | 76.2 | 0.68 | 234.8348 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 323.6813
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 714.8348
Safety factor |  |  |  |  | 10% | 71.4835
Room latent heat total | [5 empty] | 786.3183 | AS PER SPECIFICATION - TR |  |  |  | 0.5
Room total heat | [5 empty] | 6754.2773 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 323.6813
[7 empty] | AS PER DRAWING - TR |  |  |  | 0.80687
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 323.6813
OUT SIDE AIR HEAT
Sensible | 0.88 | 37.7674 | Cfm | 33.6 | 1.08 | 1206.0438
Latent | 0.88 | 37.7674 | Cfm | 76.2 | 0.68 | 1722.1221
Grand total heat ( Btu/hr) | [5 empty] | 9682.4432
Tonnage | [5 empty] | 0.80687
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## ROOM 4
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 7.1 | 23.288
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 2.9 | 9.512
Space used for |  | ROOM 4 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 23.288 | 9.512 | 221.5155 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 23.288
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.512
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 221.5155 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 2542.9974 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 36.7782 | Glass - E | 0 |  | CFM for people | 15
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 13.2909
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 28.2909
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 8.4873
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 36.7782
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 221.5155
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 221.5155 | Sq ft | 53.6 | 0.4 | 4749.2914 | [5 empty] | Partition wall | 109.1978 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 109.1978 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 109.1978 | Sq ft | 28.6 | 0.4 | 1249.2224 | [5 empty] | Out side air | 36.7782 |  | TOTAL | 109.1978 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 221.5155
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.1783
Out side air | 0.12 | 36.7782 | Cfm | 33.6 | 1.08 | 160.1529 | [5 empty] | Dehumidifed CFM | 569.9634
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 221.5155 | Watts | 3.413 |  | 756.0323
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 9341.1989 | Room sensible heat - Summer |  |  |  | 10508.8488
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1167.6499 | Room total heat |  |  |  | 11288.4011
Room sensible heat total | [5 empty] | 10508.8488 | Effective sen. heat factor |  |  |  | 0.93094
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 36.7782 | Cfm | 76.2 | 0.68 | 228.6839 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 569.9634
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 708.6839
Safety factor |  |  |  |  | 10% | 70.8684
Room latent heat total | [5 empty] | 779.5523 | AS PER SPECIFICATION - TR |  |  |  | 1
Room total heat | [5 empty] | 11288.4011 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 569.9634
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.1783
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 569.9634
OUT SIDE AIR HEAT
Sensible | 0.88 | 36.7782 | Cfm | 33.6 | 1.08 | 1174.4546
Latent | 0.88 | 36.7782 | Cfm | 76.2 | 0.68 | 1677.0156
Grand total heat ( Btu/hr) | [5 empty] | 14139.8713
Tonnage | [5 empty] | 1.1783
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## ROOM 5
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 7.1 | 23.288
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 2.9 | 9.512
Space used for |  | ROOM 5 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 23.288 | 9.512 | 221.5155 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 23.288
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.512
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 221.5155 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 2542.9974 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 36.7782 | Glass - E | 0 |  | CFM for people | 15
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 13.2909
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 28.2909
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 8.4873
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 36.7782
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 221.5155
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 221.5155 | Sq ft | 53.6 | 0.4 | 4749.2914 | [5 empty] | Partition wall | 109.1978 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 109.1978 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 109.1978 | Sq ft | 28.6 | 0.4 | 1249.2224 | [5 empty] | Out side air | 36.7782 |  | TOTAL | 109.1978 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 221.5155
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.1783
Out side air | 0.12 | 36.7782 | Cfm | 33.6 | 1.08 | 160.1529 | [5 empty] | Dehumidifed CFM | 569.9634
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 221.5155 | Watts | 3.413 |  | 756.0323
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 9341.1989 | Room sensible heat - Summer |  |  |  | 10508.8488
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1167.6499 | Room total heat |  |  |  | 11288.4011
Room sensible heat total | [5 empty] | 10508.8488 | Effective sen. heat factor |  |  |  | 0.93094
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 36.7782 | Cfm | 76.2 | 0.68 | 228.6839 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 569.9634
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 708.6839
Safety factor |  |  |  |  | 10% | 70.8684
Room latent heat total | [5 empty] | 779.5523 | AS PER SPECIFICATION - TR |  |  |  | 1
Room total heat | [5 empty] | 11288.4011 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 569.9634
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.1783
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 569.9634
OUT SIDE AIR HEAT
Sensible | 0.88 | 36.7782 | Cfm | 33.6 | 1.08 | 1174.4546
Latent | 0.88 | 36.7782 | Cfm | 76.2 | 0.68 | 1677.0156
Grand total heat ( Btu/hr) | [5 empty] | 14139.8713
Tonnage | [5 empty] | 1.1783
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## ROOM 6
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 7.1 | 23.288
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 2.9 | 9.512
Space used for |  | ROOM 6 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 23.288 | 9.512 | 221.5155 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 23.288
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.512
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 221.5155 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 2542.9974 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 36.7782 | Glass - E | 0 |  | CFM for people | 15
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 13.2909
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 28.2909
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 8.4873
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 36.7782
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 221.5155
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 221.5155 | Sq ft | 53.6 | 0.4 | 4749.2914 | [5 empty] | Partition wall | 109.1978 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 109.1978 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 109.1978 | Sq ft | 28.6 | 0.4 | 1249.2224 | [5 empty] | Out side air | 36.7782 |  | TOTAL | 109.1978 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 221.5155
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.1783
Out side air | 0.12 | 36.7782 | Cfm | 33.6 | 1.08 | 160.1529 | [5 empty] | Dehumidifed CFM | 569.9634
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 221.5155 | Watts | 3.413 |  | 756.0323
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 9341.1989 | Room sensible heat - Summer |  |  |  | 10508.8488
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1167.6499 | Room total heat |  |  |  | 11288.4011
Room sensible heat total | [5 empty] | 10508.8488 | Effective sen. heat factor |  |  |  | 0.93094
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 36.7782 | Cfm | 76.2 | 0.68 | 228.6839 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 569.9634
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 708.6839
Safety factor |  |  |  |  | 10% | 70.8684
Room latent heat total | [5 empty] | 779.5523 | AS PER SPECIFICATION - TR |  |  |  | 1
Room total heat | [5 empty] | 11288.4011 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 569.9634
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.1783
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 569.9634
OUT SIDE AIR HEAT
Sensible | 0.88 | 36.7782 | Cfm | 33.6 | 1.08 | 1174.4546
Latent | 0.88 | 36.7782 | Cfm | 76.2 | 0.68 | 1677.0156
Grand total heat ( Btu/hr) | [5 empty] | 14139.8713
Tonnage | [5 empty] | 1.1783
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## ROOM 7
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 7.1 | 23.288
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 2.9 | 9.512
Space used for |  | ROOM 7 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 23.288 | 9.512 | 221.5155 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 23.288
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.512
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 221.5155 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 2542.9974 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 36.7782 | Glass - E | 0 |  | CFM for people | 15
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 13.2909
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 28.2909
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 8.4873
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 36.7782
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 221.5155
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 221.5155 | Sq ft | 53.6 | 0.4 | 4749.2914 | [5 empty] | Partition wall | 109.1978 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 109.1978 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 109.1978 | Sq ft | 28.6 | 0.4 | 1249.2224 | [5 empty] | Out side air | 36.7782 |  | TOTAL | 109.1978 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 221.5155
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.1783
Out side air | 0.12 | 36.7782 | Cfm | 33.6 | 1.08 | 160.1529 | [5 empty] | Dehumidifed CFM | 569.9634
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 221.5155 | Watts | 3.413 |  | 756.0323
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 9341.1989 | Room sensible heat - Summer |  |  |  | 10508.8488
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1167.6499 | Room total heat |  |  |  | 11288.4011
Room sensible heat total | [5 empty] | 10508.8488 | Effective sen. heat factor |  |  |  | 0.93094
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 36.7782 | Cfm | 76.2 | 0.68 | 228.6839 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 569.9634
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 708.6839
Safety factor |  |  |  |  | 10% | 70.8684
Room latent heat total | [5 empty] | 779.5523 | AS PER SPECIFICATION - TR |  |  |  | 1
Room total heat | [5 empty] | 11288.4011 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 569.9634
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.1783
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 569.9634
OUT SIDE AIR HEAT
Sensible | 0.88 | 36.7782 | Cfm | 33.6 | 1.08 | 1174.4546
Latent | 0.88 | 36.7782 | Cfm | 76.2 | 0.68 | 1677.0156
Grand total heat ( Btu/hr) | [5 empty] | 14139.8713
Tonnage | [5 empty] | 1.1783
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## ROOM 8
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 7.1 | 23.288
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 2.9 | 9.512
Space used for |  | ROOM 8 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 23.288 | 9.512 | 221.5155 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 23.288
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.512
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 221.5155 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 2542.9974 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 36.7782 | Glass - E | 0 |  | CFM for people | 15
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 13.2909
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 28.2909
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 8.4873
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 36.7782
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 221.5155
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 221.5155 | Sq ft | 53.6 | 0.4 | 4749.2914 | [5 empty] | Partition wall | 109.1978 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 109.1978 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 109.1978 | Sq ft | 28.6 | 0.4 | 1249.2224 | [5 empty] | Out side air | 36.7782 |  | TOTAL | 109.1978 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 221.5155
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.1783
Out side air | 0.12 | 36.7782 | Cfm | 33.6 | 1.08 | 160.1529 | [5 empty] | Dehumidifed CFM | 569.9634
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 221.5155 | Watts | 3.413 |  | 756.0323
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 9341.1989 | Room sensible heat - Summer |  |  |  | 10508.8488
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1167.6499 | Room total heat |  |  |  | 11288.4011
Room sensible heat total | [5 empty] | 10508.8488 | Effective sen. heat factor |  |  |  | 0.93094
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 36.7782 | Cfm | 76.2 | 0.68 | 228.6839 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 569.9634
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 708.6839
Safety factor |  |  |  |  | 10% | 70.8684
Room latent heat total | [5 empty] | 779.5523 | AS PER SPECIFICATION - TR |  |  |  | 1
Room total heat | [5 empty] | 11288.4011 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 569.9634
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.1783
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 569.9634
OUT SIDE AIR HEAT
Sensible | 0.88 | 36.7782 | Cfm | 33.6 | 1.08 | 1174.4546
Latent | 0.88 | 36.7782 | Cfm | 76.2 | 0.68 | 1677.0156
Grand total heat ( Btu/hr) | [5 empty] | 14139.8713
Tonnage | [5 empty] | 1.1783
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## ROOM 9
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 7.1 | 23.288
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 2.9 | 9.512
Space used for |  | ROOM 9 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 23.288 | 9.512 | 221.5155 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 23.288
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 9.512
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 221.5155 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 2542.9974 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 0 | Sq ft | 12 | 0.56 | 0 | Ventilation air quantity cfm |  |  |  | 36.7782 | Glass - E | 0 |  | CFM for people | 15
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 3 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 13.2909
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 28.2909
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 0 |  | SAFETY 30% | 8.4873
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 36.7782
Wall - E |  | 0 | Sq ft | 36.6 | 0.34 | 0 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 221.5155
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 0 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 221.5155 | Sq ft | 53.6 | 0.4 | 4749.2914 | [5 empty] | Partition wall | 376.544 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 109.1978 | 0
All glass |  | 0 | Sq ft | 33.6 | 1.13 | 0 | [5 empty] | Floor | 0 |  | S | 267.3462 | 0
Partition wall |  | 376.544 | Sq ft | 28.6 | 0.4 | 4307.6634 | [5 empty] | Out side air | 36.7782 |  | TOTAL | 376.544 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 3
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 0.5
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 221.5155
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 1.4651
Out side air | 0.12 | 36.7782 | Cfm | 33.6 | 1.08 | 160.1529 | [5 empty] | Dehumidifed CFM | 756.5775
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 1.5
People |  | 3 | Nos | 240 |  | 720
Equipment |  | 0.5 | KW | 3413 | 1 | 1706.5
Lights |  | 221.5155 | Watts | 3.413 |  | 756.0323
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 12399.6399 | Room sensible heat - Summer |  |  |  | 13949.5949
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 1549.955 | Room total heat |  |  |  | 14729.1472
Room sensible heat total | [5 empty] | 13949.5949 | Effective sen. heat factor |  |  |  | 0.94707
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 36.7782 | Cfm | 76.2 | 0.68 | 228.6839 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 3 | Nos | 160 |  | 480 | Dehumidifed CFM |  |  |  | 756.5775
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 708.6839
Safety factor |  |  |  |  | 10% | 70.8684
Room latent heat total | [5 empty] | 779.5523 | AS PER SPECIFICATION - TR |  |  |  | 1.5
Room total heat | [5 empty] | 14729.1472 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 756.5775
[7 empty] | AS PER DRAWING - TR |  |  |  | 1.4651
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 756.5775
OUT SIDE AIR HEAT
Sensible | 0.88 | 36.7782 | Cfm | 33.6 | 1.08 | 1174.4546
Latent | 0.88 | 36.7782 | Cfm | 76.2 | 0.68 | 1677.0156
Grand total heat ( Btu/hr) | [5 empty] | 17580.6174
Tonnage | [5 empty] | 1.4651
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## ROOM 10
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 18 | 59.04
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 7.1 | 23.288
Space used for |  | ROOM 10 |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 59.04 | 23.288 | 1374.9235 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 59.04
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 23.288
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 1374.9235 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 15784.122 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 5
Glass - E |  | 120 | Sq ft | 12 | 0.56 | 806.4 | Ventilation air quantity cfm |  |  |  | 172.244 | Glass - E | 120 |  | CFM for people | 50
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 10 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 0 | Sq ft | 12 | 0.56 | 0 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 0 |  | CFM for Area basis | 82.4954
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 132.4954
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 557.7792 |  | SAFETY 30% | 39.7486
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 172.244
Wall - E |  | 557.7792 | Sq ft | 36.6 | 0.34 | 6941.0044 | [5 empty] | Wall - S | 0
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 1374.9235
Wall - S |  | 0 | Sq ft | 34.6 | 0.34 | 0 | [5 empty] | All glass | 120 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 1374.9235 | Sq ft | 53.6 | 0.4 | 29478.3603 | [5 empty] | Partition wall | 0 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 0 | 0
All glass |  | 120 | Sq ft | 33.6 | 1.13 | 4556.16 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 0 | Sq ft | 28.6 | 0.4 | 0 | [5 empty] | Out side air | 172.244 |  | TOTAL | 0 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 10
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 1
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 1374.9235
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 6.33
Out side air | 0.12 | 172.244 | Cfm | 33.6 | 1.08 | 750.047 | [5 empty] | Dehumidifed CFM | 3236.146
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 6.5
People |  | 10 | Nos | 240 |  | 2400
Equipment |  | 1 | KW | 3413 | 1 | 3413
Lights |  | 1374.9235 | Watts | 3.413 |  | 4692.614
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 53037.5856 | Room sensible heat - Summer |  |  |  | 59667.2838
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 6629.6982 | Room total heat |  |  |  | 62605.3834
Room sensible heat total | [5 empty] | 59667.2838 | Effective sen. heat factor |  |  |  | 0.95307
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 172.244 | Cfm | 76.2 | 0.68 | 1070.9996 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 10 | Nos | 160 |  | 1600 | Dehumidifed CFM |  |  |  | 3236.146
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 2670.9996
Safety factor |  |  |  |  | 10% | 267.1
Room latent heat total | [5 empty] | 2938.0996 | AS PER SPECIFICATION - TR |  |  |  | 6.5
Room total heat | [5 empty] | 62605.3834 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 3236.146
[7 empty] | AS PER DRAWING - TR |  |  |  | 6.33
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 3236.146
OUT SIDE AIR HEAT
Sensible | 0.88 | 172.244 | Cfm | 33.6 | 1.08 | 5500.3445
Latent | 0.88 | 172.244 | Cfm | 76.2 | 0.68 | 7853.9973
Grand total heat ( Btu/hr) | [5 empty] | 75959.7252
Tonnage | [5 empty] | 6.33
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED

## DEMONSTRATION OF SKILL
HEAT LOAD ESTIMATION @ ASHRAE STD
Estimated by |  | RITHVIK CONSULTANTS | [10 empty] | In Mtr | in Ft
Job name |  | PSP HOSPITAL |  |  |  |  | Estimate for Summer |  |  | Peak time : 4 pm |  | Length | 13.8 | 45.264
Place |  | CHENNAI |  |  |  |  | Conditions | DB oF | WB oF | % RH | Gr/lb | Breadth | 6 | 19.68
Space used for |  | DEMONSTRATION OF SKILL |  |  |  |  | Out side | 107 | 84.4 | 40 | 143.9 | Height | 3.5 | 11.48
Size in Ft. & Area in Sq. Ft. |  | Lt. Ft. | Br. Ft. | Area sq. ft | Ht. Ft. | Dailyrange | Room Cond. | 73.4 | 62.6 | 55 | 67.7
|  | 45.264 | 19.68 | 890.7955 | 11.48 | 18 deg F | Difference | 33.6 | XXXXX | XXXXX | 76.2 | Lt. Ft. | 45.264
Item |  | Area/Qty |  | Sun gain/ | Factor | Btu/hr | By-pass factor |  |  |  | 0.12 | Br. Ft. | 19.68
|  |  |  | Temp diff deg F |  |  | VENTILATION |  |  |  |  | Area sq. ft | 890.7955 |  | Ventilation Air Quantity - Minimum
SUN GAIN - GLASS | [6 empty] | Total Volume of air |  |  |  | 10226.3326 | Ht. Ft. | 11.48 |  | 5 CFM PER PERSON + | 0.06 CFM PER SQ FEET
Glass - N |  | 0 | Sq ft | 23 | 0.56 | 0 | No of air changes per hour |  |  |  | 0 | Glass - N | 0 |  | CFM/person | 7.5
Glass - E |  | 40 | Sq ft | 12 | 0.56 | 268.8 | Ventilation air quantity cfm |  |  |  | 118.2321 | Glass - E | 40 |  | CFM for people | 37.5
Glass - W |  | 0 | Sq ft | 163 | 0.56 | 0 | No.of Person | 5 |  |  | 0 | Glass- W | 0 |  | CFm per sqft | 0.06
Glass - S |  | 80 | Sq ft | 12 | 0.56 | 537.6 | With Air change Vent Air CFM Reqd |  |  |  | 0 | Glass - S | 80 |  | CFM for Area basis | 53.4477
[12 empty] | Wall - N | 0 |  | Total Air Quantity | 90.9477
SOLAR & TRANSMISSION GAIN-WALLS & ROOF | [11 empty] | Wall - E | 185.9264 |  | SAFETY 30% | 27.2843
Wall - N |  | 0 | Sq ft | 22.6 | 0.34 | 0 | [5 empty] | Wall - W | 0 |  | MIN FA REQT | 118.2321
Wall - E |  | 185.9264 | Sq ft | 36.6 | 0.34 | 2313.6681 | [5 empty] | Wall - S | 439.6307
Wall - W |  | 0 | Sq ft | 30.6 | 0.34 | 0 | [5 empty] | Roof - Exposed | 890.7955
Wall - S |  | 439.6307 | Sq ft | 34.6 | 0.34 | 5171.8158 | [5 empty] | All glass | 120 |  |  | P-WALL | P-GLASS
Roof - Exposed |  | 890.7955 | Sq ft | 53.6 | 0.4 | 19098.6559 | [5 empty] | Partition wall | 225.9264 |  | N | 0 | 0
[12 empty] | Partition glass | 0 |  | E | 0 | 0
TRANSMISSION GAIN - EXCEPT WALLS & ROOF | [11 empty] | Ceiling | 0 |  | W | 225.9264 | 0
All glass |  | 120 | Sq ft | 33.6 | 1.13 | 4556.16 | [5 empty] | Floor | 0 |  | S | 0 | 0
Partition wall |  | 225.9264 | Sq ft | 28.6 | 0.4 | 2584.598 | [5 empty] | Out side air | 118.2321 |  | TOTAL | 225.9264 | 0
Partition glass |  | 0 | Sq ft | 28.6 | 1.1 | 0 | [5 empty] | People | 5
Ceiling |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Equipment | 2
Floor |  | 0 | Sq ft | 33.6 | 0.4 | 0 | [5 empty] | Lights | 890.7955
INFILTRATOIN & OUTSIDE AIR
[12 empty] | Tonnage | 5.2277
Out side air | 0.12 | 118.2321 | Cfm | 33.6 | 1.08 | 514.8486 | [5 empty] | Dehumidifed CFM | 2813.6002
INTERNAL HEAT | [11 empty] | RECOMMENDED TR | 5.5
People |  | 5 | Nos | 240 |  | 1200
Equipment |  | 2 | KW | 3413 | 1 | 6826
Lights |  | 890.7955 | Watts | 3.413 |  | 3040.2851
DEHUMIDIFIED AIR QUANTITY
Room sensible heat sub total | [5 empty] | 46112.4315 | Room sensible heat - Summer |  |  |  | 51876.4855
S.A duct heat gain+fan gain+Safety factor |  |  |  |  | 12.5% | 5764.0539 | Room total heat |  |  |  | 53565.1587
Room sensible heat total | [5 empty] | 51876.4855 | Effective sen. heat factor |  |  |  | 0.96847
[7 empty] | Indicated ADP |  |  |  | 54
ROOM LATENT HEAT | [6 empty] | Selected ADP |  |  |  | 54
Outside air | 0.12 | 118.2321 | Cfm | 76.2 | 0.68 | 735.1574 | Dehumidified rise in deg F |  |  |  | 17.072
People |  | 5 | Nos | 160 |  | 800 | Dehumidifed CFM |  |  |  | 2813.6002
Steam |  | 0 | kg/hr | 2418.8 |  | 0
Room Latent heat sub total | [5 empty] | 1535.1574
Safety factor |  |  |  |  | 10% | 153.5157
Room latent heat total | [5 empty] | 1688.6732 | AS PER SPECIFICATION - TR |  |  |  | 5.5
Room total heat | [5 empty] | 53565.1587 | AS PER SPECIFICATION AIR QTY IN CFM |  |  |  | 2813.6002
[7 empty] | AS PER DRAWING - TR |  |  |  | 5.2277
[7 empty] | AS PER DRAWING AIR QTY IN CFM |  |  |  | 2813.6002
OUT SIDE AIR HEAT
Sensible | 0.88 | 118.2321 | Cfm | 33.6 | 1.08 | 3775.5561
Latent | 0.88 | 118.2321 | Cfm | 76.2 | 0.68 | 5391.1545
Grand total heat ( Btu/hr) | [5 empty] | 62731.8693
Tonnage | [5 empty] | 5.2277
NOTE:
THE FLOOR ABOVE THE CONDITION SPACE ARE ASSUMED TO BE NON AIR CONDITIONED